## BMS fault
Fault ID | Mall Name | Level | Asset ID | Category Impact | Category Fault | Sub Category Fault | Equipment Affected | Diagnostics | Open Datetime | Duration | Close Datetime | Potential Saving (kWh) | Status | Equipement Status | Potential Saving ($)
1 | Century Square | Level 1 | Sensor 05 | Energy | Control | AHU | 8 | Fault Static Pressure Sensor | 2024-02-29 09:39 | 3d 18h 30m | 2024-02-29 09:39 | 0 | Closed | Online | 0
2 | Century Square | Level 3 | AHU002 | Energy | Control | CH | 30 | AHU VSD is not modulating | 2024-03-01 09:39 | 13d 16h 45m | 2024-03-01 09:39 | 0 | Closed | Offline | 0
3 | Century Square | Level B2 | AHU003 | Energy | Control | CHWP | 1 | Air Damper is not modulating | 2024-03-02 09:39 | 2h 10m | 2024-03-02 09:39 | 0 | Closed | Online | 0
4 | Century Square | Level B1 | AHU004 | Energy | Control | CHPL | 2 | AHU is operating outside operation | 2024-03-03 09:39 | 7d 14h 25m | 2024-03-03 09:39 | 35.5 | Closed | Offline | 2.627
5 | Century Square | Level 1 | AHU005 | Energy | Control | CT | 40 | AHU high VSD Speed (Default >40Hz User defined) | 2024-03-04 09:39 | 12d 23h 20m | 2024-03-04 09:39 | 620 | Closed | Online | 45.88
6 | Century Square | Level 3 | Sensor 06 | Energy | Control | CWP | 3 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-03-05 09:39 | 7d 14h 25m | 2024-03-05 09:39 | 28 | Closed | Offline | 2.072
7 | Century Square | Level 3 | Sensor 07 | Energy | Control | AHU | 8 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-03-06 09:39 | 6d 0h 35m | 2024-03-06 09:39 | 20 | Closed | Online | 1.48
8 | Century Square | Level 4 | Sensor 08 | Energy | Control | AHU | 1 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-03-07 09:39 | 37d 9h 25m | 2024-03-07 09:39 | 5 | Closed | Offline | 0.37
9 | Century Square | Level B2 | Sensor 06 | Energy | Control | AHU | 3 | CHW CV not modulating (Out of Range/Stucked) | 2024-03-08 09:39 | 16d 8h 55m | 2024-03-08 09:39 | 30 | Closed | Online | 2.22
10 | Century Square | Level 4 | AHU006 | Energy | Control | AHU | 5 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-03-09 09:39 | 1d 22h 50m | 2024-03-09 09:39 | 0 | Closed | Online | 0
11 | Century Square | Level B1 | AHU007 | Energy | Control | AHU | 2 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-03-10 09:39 | 5d 3h 50m | 2024-03-10 09:39 | 0 | Closed | Online | 0
12 | Century Square | Level 3 | AHU008 | Energy | Control | AHU | 1 | Fault Static Pressure Sensor | 2024-03-11 09:39 | 1d 2h 50m | 2024-03-11 09:39 | 35 | Closed | Online | 2.59
13 | Century Square | Level 4 | AHU009 | Energy | Control | AHU | 2 | AHU VSD is not modulating | 2024-03-12 09:39 | 7d 22h 50m | 2024-03-12 09:39 | 23 | Closed | Online | 1.702
14 | Century Square | Level 2 | Sensor 09 | Energy | Control | AHU | 5 | Air Damper is not modulating | 2024-03-13 09:39 | 6d 28h 2m | 2024-03-13 09:39 | 0 | Closed | Online | 0
15 | Century Square | Level B1 | Sensor 10 | Energy | Control | AHU | 6 | AHU is operating outside operation | 2024-03-14 09:39 | 3d 18h 30m | 2024-03-14 09:39 | 0 | Closed | Online | 0
16 | Century Square | Level 1 | Sensor 11 | Energy | Control | AHU | 8 | AHU high VSD Speed (Default >40Hz User defined) | 2024-03-15 09:39 | 13d 16h 45m | 2024-03-15 09:39 | 56 | Closed | Online | 4.144
17 | Century Square | Level 3 | Sensor 07 | Energy | Control | AHU | 20 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-03-16 09:39 | 2h 10m | 2024-03-16 09:39 | 0 | Closed | Online | 0
18 | Century Square | Level B1 | AHU010 | Energy | Control | AHU | 15 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-03-17 09:39 | 7d 14h 25m | 2024-03-17 09:39 | 69 | Closed | Online | 5.106
19 | Century Square | Level B1 | AHU011 | Energy | Control | AHU | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-03-18 09:39 | 12d 23h 20m | 2024-03-18 09:39 | 100 | Closed | Online | 7.4
20 | Century Square | Level B1 | AHU012 | Energy | Control | AHU | 4 | CHW CV not modulating (Out of Range/Stucked) | 2024-03-19 09:39 | 7d 14h 25m | 2024-03-19 09:39 | 35 | Closed | Offline | 2.59
21 | Century Square | Level 4 | AHU013 | Energy | Control | AHU | 5 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-03-20 09:39 | 6d 0h 35m | 2024-03-20 09:39 | 7 | Closed | Offline | 0.518
22 | Century Square | Level 3 | Sensor 12 | Energy | Control | CH | 16 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-03-21 09:39 | 37d 9h 25m | 2024-03-21 09:39 | 60 | Closed | Offline | 4.44
23 | Century Square | Level B1 | Sensor 13 | Energy | Control | CH | 20 | Fault Static Pressure Sensor | 2024-03-22 09:39 | 16d 8h 55m | 2024-03-22 09:39 | 0 | Closed | Online | 0
24 | Century Square | Level 3 | Sensor 14 | Energy | Control | CH | 2 | AHU VSD is not modulating | 2024-03-23 09:39 | 1d 22h 50m | 2024-03-23 09:39 | 120 | Closed | Online | 8.88
25 | Century Square | Level 4 | Sensor 08 | Energy | Control | CHWP | 3 | Air Damper is not modulating | 2024-03-24 09:39 | 5d 3h 50m | 2024-03-24 09:39 | 0 | Closed | Online | 0
26 | Century Square | Level B1 | AHU014 | Energy | Control | CHWP | 1 | AHU is operating outside operation | 2024-03-25 09:39 | 1d 2h 50m | 2024-03-25 09:39 | 0 | Closed | Online | 0
27 | Century Square | Level 4 | AHU015 | Energy | Control | CHWP | 25 | AHU high VSD Speed (Default >40Hz User defined) | 2024-03-26 09:39 | 7d 22h 50m | 2024-03-26 09:39 | 0 | Closed | Online | 0
28 | Century Square | Level B1 | AHU016 | Energy | Control | CHWP | 7 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-03-27 09:39 | 6d 28h 2m | 2024-03-27 09:39 | 0 | Closed | Online | 0
29 | Century Square | Level 4 | AHU017 | Energy | Sensor | CHPL | 8 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-03-28 09:39 | 3d 18h 30m | 2024-03-28 09:39 | 0 | Closed | Online | 0
30 | Century Square | Level 3 | Sensor 15 | Energy | Sensor | CHPL | 30 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-03-29 09:39 | 13d 16h 45m | 2024-03-29 09:39 | 62.1 | Closed | Online | 4.5954
31 | Century Square | Level 3 | Sensor 16 | Energy | Sensor | CT | 1 | CHW CV not modulating (Out of Range/Stucked) | 2024-03-30 09:39 | 2h 10m | 2024-03-30 09:39 | 0 | Closed | Online | 0
32 | Century Square | Level 4 | Sensor 17 | Energy | Sensor | CT | 2 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-03-31 09:39 | 7d 14h 25m | 2024-03-31 09:39 | 0 | Closed | Online | 0
33 | Century Square | Level 1 | Sensor 09 | Energy | Sensor | CT | 40 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-04-01 09:39 | 12d 23h 20m | 2024-04-01 09:39 | 0 | Closed | Online | 0
34 | Century Square | Level 4 | AHU018 | Energy | Sensor | CT | 3 | Fault Static Pressure Sensor | 2024-04-02 09:39 | 7d 14h 25m | 2024-04-02 09:39 | 21.5 | Closed | Online | 1.591
35 | Century Square | Level 1 | AHU019 | Energy | Sensor | CT | 8 | AHU VSD is not modulating | 2024-04-03 09:39 | 6d 0h 35m | 2024-04-03 09:39 | 2 | Closed | Online | 0.148
36 | Century Square | Level 4 | AHU020 | Energy | Service | CT | 1 | Air Damper is not modulating | 2024-04-04 09:39 | 37d 9h 25m | 2024-04-04 09:39 | 0 | Closed | Offline | 0
37 | Century Square | Level 4 | AHU021 | Energy | Service | CT | 3 | AHU is operating outside operation | 2024-04-05 09:39 | 16d 8h 55m | 2024-04-05 09:39 | 0 | Closed | Offline | 0
38 | Century Square | Level 4 | Sensor 18 | Energy | Service | CWP | 5 | AHU high VSD Speed (Default >40Hz User defined) | 2024-04-06 09:39 | 1d 22h 50m | 2024-04-06 09:39 | 0 | Closed | Online | 0
39 | Century Square | Level 3 | Sensor 19 | Energy | Service | CWP | 2 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-04-07 09:39 | 5d 3h 50m | 2024-04-07 09:39 | 0 | Closed | Online | 0
40 | Century Square | Level 3 | Sensor 20 | Energy | Service | CWP | 1 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-04-08 09:39 | 1d 2h 50m | 2024-04-08 09:39 | 0 | Open | Online | 0
41 | Century Square | Level 4 | Sensor 10 | Energy | Control | AHU | 2 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-04-09 09:39 | 7d 22h 50m | 2024-04-09 09:39 | 21.6 | Open | Online | 1.5984
42 | Century Square | Level B1 | AHU022 | Energy | Control | AHU | 5 | CHW CV not modulating (Out of Range/Stucked) | 2024-04-10 09:39 | 6d 28h 2m | 2024-04-10 09:39 | 3 | Open | Online | 0.222
43 | Century Square | Level 3 | AHU023 | Energy | Control | AHU | 6 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-04-11 09:39 | 3d 18h 30m | 2024-04-11 09:39 | 0 | In-Progress | Online | 0
44 | Century Square | Level 4 | AHU024 | Energy | Control | AHU | 8 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-04-12 09:39 | 13d 16h 45m | 2024-04-12 09:39 | 0 | In-Progress | Online | 0
45 | Century Square | Level 4 | AHU025 | Energy | Control | AHU | 20 | Fault Static Pressure Sensor | 2024-04-13 09:39 | 2h 10m | 2024-04-13 09:39 | 0 | In-Progress | Online | 0
46 | Century Square | Level 3 | Sensor 21 | Energy | Control | AHU | 15 | AHU VSD is not modulating | 2024-04-14 09:39 | 7d 14h 25m | 2024-04-14 09:39 | 0 | In-Progress | Online | 0
47 | Century Square | Level 3 | Sensor 22 | Energy | Control | AHU | 5 | Air Damper is not modulating | 2024-04-15 09:39 | 12d 23h 20m | 2024-04-15 09:39 | 35.5 | In-Progress | Online | 2.627
48 | Century Square | Level 3 | Sensor 23 | Energy | Control | AHU | 4 | AHU is operating outside operation | 2024-04-16 09:39 | 7d 14h 25m | 2024-04-16 09:39 | 620 | Closed | Online | 45.88
49 | Century Square | Level B1 | Sensor 11 | Energy | Control | AHU | 5 | AHU high VSD Speed (Default >40Hz User defined) | 2024-04-17 09:39 | 6d 0h 35m | 2024-04-17 09:39 | 28 | Closed | Online | 2.072
50 | Century Square | Level 1 | AHU026 | Operation | Control | AHU | 16 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-04-18 09:39 | 37d 9h 25m | 2024-04-18 09:39 | 20 | In-Progress | Offline | 1.48
51 | Century Square | Level 3 | AHU027 | Comfort | Control | AHU | 20 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-04-19 09:39 | 16d 8h 55m | 2024-04-19 09:39 | 5 | In-Progress | Online | 0.37
52 | Century Square | Level 1 | AHU028 | Comfort | Control | AHU | 2 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-04-20 09:39 | 1d 22h 50m | 2024-04-20 09:39 | 30 | In-Progress | Online | 2.22
53 | Century Square | Level 3 | AHU029 | Comfort | Control | AHU | 3 | CHW CV not modulating (Out of Range/Stucked) | 2024-04-21 09:39 | 5d 3h 50m | 2024-04-21 09:39 | 0 | In-Progress | Online | 0
54 | Century Square | Level 4 | Sensor 24 | Comfort | Control | AHU | 1 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-04-22 09:39 | 1d 2h 50m | 2024-04-22 09:39 | 0 | Closed | Online | 0
55 | Century Square | Level 4 | Sensor 25 | Comfort | Control | AHU | 25 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-04-23 09:39 | 7d 22h 50m | 2024-04-23 09:39 | 35 | Closed | Online | 2.59
56 | Century Square | Level 5 | Sensor 26 | Comfort | Control | CH | 7 | Fault Static Pressure Sensor | 2024-04-24 09:39 | 6d 28h 2m | 2024-04-24 09:39 | 23 | Closed | Online | 1.702
57 | Century Square | Level 1 | Sensor 12 | Comfort | Control | CH | 1 | AHU VSD is not modulating | 2024-04-25 09:39 | 3d 18h 30m | 2024-04-25 09:39 | 0 | Closed | Online | 0
58 | Century Square | Level 1 | AHU030 | Comfort | Control | CH | 3 | Air Damper is not modulating | 2024-04-26 09:39 | 13d 16h 45m | 2024-04-26 09:39 | 0 | Closed | Online | 0
59 | Century Square | Level 1 | AHU031 | Comfort | Control | CHWP | 5 | AHU is operating outside operation | 2024-04-27 09:39 | 2h 10m | 2024-04-27 09:39 | 56 | Closed | Online | 4.144
60 | Century Square | Level 5 | AHU032 | Comfort | Control | CHWP | 2 | AHU high VSD Speed (Default >40Hz User defined) | 2024-04-28 09:39 | 7d 14h 25m | 2024-04-28 09:39 | 0 | Closed | Online | 0
61 | Century Square | Level 1 | AHU033 | Comfort | Control | CHWP | 1 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-04-29 09:39 | 12d 23h 20m | 2024-04-29 09:39 | 69 | Closed | Online | 5.106
62 | Century Square | Level 1 | Sensor 27 | Comfort | Control | CHWP | 2 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-04-30 09:39 | 7d 14h 25m | 2024-04-30 09:39 | 100 | Closed | Online | 7.4
63 | Century Square | Level 1 | Sensor 28 | Comfort | Control | CHPL | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-05-01 09:39 | 6d 0h 35m | 2024-05-01 09:39 | 35 | Closed | Offline | 2.59
64 | Century Square | Level 1 | Sensor 29 | Comfort | Control | CHPL | 6 | CHW CV not modulating (Out of Range/Stucked) | 2024-05-02 09:39 | 37d 9h 25m | 2024-05-02 09:39 | 7 | Closed | Online | 0.518
65 | Century Square | Level 3 | Sensor 13 | Comfort | Control | CT | 8 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-05-03 09:39 | 16d 8h 55m | 2024-05-03 09:39 | 60 | Closed | Online | 4.44
66 | Causeway Point | Level 1 | AHU034 | Comfort | Control | CT | 20 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-05-04 09:39 | 1d 22h 50m | 2024-05-04 09:39 | 0 | Closed | Online | 0
67 | Causeway Point | Level 3 | AHU035 | Comfort | Control | CT | 15 | Fault Static Pressure Sensor | 2024-05-05 09:39 | 5d 3h 50m | 2024-05-05 09:39 | 120 | Closed | Online | 8.88
68 | Causeway Point | Level 4 | AHU036 | Comfort | Control | CT | 5 | AHU VSD is not modulating | 2024-05-06 09:39 | 1d 2h 50m | 2024-05-06 09:39 | 0 | Closed | Online | 0
69 | Causeway Point | Level B2 | AHU037 | Comfort | Control | CT | 4 | Air Damper is not modulating | 2024-05-07 09:39 | 7d 22h 50m | 2024-05-07 09:39 | 0 | Closed | Online | 0
70 | Causeway Point | Level 3 | Sensor 30 | Comfort | Control | CT | 5 | AHU is operating outside operation | 2024-05-08 09:39 | 6d 28h 2m | 2024-05-08 09:39 | 0 | Closed | Online | 0
71 | Causeway Point | Level B1 | Sensor 31 | Comfort | Control | CT | 16 | AHU high VSD Speed (Default >40Hz User defined) | 2024-05-09 09:39 | 3d 18h 30m | 2024-05-09 09:39 | 0 | Closed | Online | 0
72 | Causeway Point | Level 3 | Sensor 32 | Comfort | Control | CWP | 20 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-05-10 09:39 | 13d 16h 45m | 2024-05-10 09:39 | 0 | Closed | Online | 0
73 | Causeway Point | Level B2 | Sensor 14 | Comfort | Control | CWP | 2 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-05-11 09:39 | 2h 10m | 2024-05-11 09:39 | 62.1 | Closed | Online | 4.5954
74 | Causeway Point | Level 4 | AHU038 | Comfort | Control | CHWP | 3 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-05-12 09:39 | 7d 14h 25m | 2024-05-12 09:39 | 0 | Closed | Online | 0
75 | Causeway Point | Level 3 | AHU039 | Comfort | Control | CHWP | 1 | CHW CV not modulating (Out of Range/Stucked) | 2024-05-13 09:39 | 12d 23h 20m | 2024-05-13 09:39 | 0 | Closed | Online | 0
76 | Causeway Point | Level 3 | AHU040 | Comfort | Control | CHPL | 25 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-05-14 09:39 | 7d 14h 25m | 2024-05-14 09:39 | 0 | Closed | Offline | 0
77 | Causeway Point | Level 1 | AHU041 | Comfort | Control | CHPL | 7 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-05-15 09:39 | 6d 0h 35m | 2024-05-15 09:39 | 21.5 | Closed | Online | 1.591
78 | Causeway Point | Level 4 | Sensor 33 | Comfort | Control | CT | 8 | Fault Static Pressure Sensor | 2024-05-16 09:39 | 37d 9h 25m | 2024-05-16 09:39 | 2 | Closed | Online | 0.148
79 | Causeway Point | Level 4 | Sensor 34 | Comfort | Control | CT | 30 | AHU VSD is not modulating | 2024-05-17 09:39 | 16d 8h 55m | 2024-05-17 09:39 | 0 | Closed | Online | 0
80 | Causeway Point | Level B2 | Sensor 35 | Comfort | Control | CT | 1 | Air Damper is not modulating | 2024-05-18 09:39 | 1d 22h 50m | 2024-05-18 09:39 | 0 | Closed | Online | 0
81 | Causeway Point | Level B1 | Sensor 15 | Comfort | Control | CT | 2 | AHU is operating outside operation | 2024-05-19 09:39 | 5d 3h 50m | 2024-05-19 09:39 | 0 | Closed | Online | 0
82 | Causeway Point | Level 4 | AHU042 | Operation | Control | CT | 40 | AHU high VSD Speed (Default >40Hz User defined) | 2024-05-20 09:39 | 1d 2h 50m | 2024-05-20 09:39 | 0 | Closed | Online | 0
83 | Causeway Point | Level 4 | AHU043 | Operation | Control | CT | 3 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-05-21 09:39 | 7d 22h 50m | 2024-05-21 09:39 | 0 | Closed | Online | 0
84 | Causeway Point | Level 3 | AHU044 | Operation | Control | CT | 8 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-05-22 09:39 | 6d 28h 2m | 2024-05-22 09:39 | 21.6 | Closed | Online | 1.5984
85 | Causeway Point | Level 4 | AHU045 | Operation | Control | CWP | 1 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-05-23 09:39 | 3d 18h 30m | 2024-05-23 09:39 | 3 | Closed | Online | 0.222
86 | Causeway Point | Level 3 | Sensor 36 | Operation | Control | CWP | 3 | CHW CV not modulating (Out of Range/Stucked) | 2024-05-24 09:39 | 13d 16h 45m | 2024-05-24 09:39 | 0 | Closed | Online | 0
87 | Causeway Point | Level 4 | Sensor 37 | Operation | Control | CWP | 5 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-05-25 09:39 | 2h 10m | 2024-05-25 09:39 | 0 | Closed | Online | 0
88 | Causeway Point | Level 1 | Sensor 38 | Operation | Control | AHU | 2 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-05-26 09:39 | 7d 14h 25m | 2024-05-26 09:39 | 0 | Closed | Online | 0
89 | Causeway Point | Level 3 | Sensor 16 | Operation | Sensor | AHU | 1 | AHU VSD is not modulating | 2024-05-27 09:39 | 12d 23h 20m | 2024-05-27 09:39 | 0 | Closed | Offline | 0
90 | Causeway Point | Level 1 | AHU046 | Operation | Sensor | AHU | 2 | Air Damper is not modulating | 2024-05-28 09:39 | 7d 14h 25m | 2024-05-28 09:39 | 35.5 | Closed | Online | 2.627
91 | Causeway Point | Level 3 | AHU047 | Operation | Sensor | AHU | 5 | AHU is operating outside operation | 2024-05-29 09:39 | 6d 0h 35m | 2024-05-29 09:39 | 620 | Closed | Online | 45.88
92 | Causeway Point | Level 1 | AHU048 | Operation | Sensor | AHU | 8 | AHU high VSD Speed (Default >40Hz User defined) | 2024-05-30 09:39 | 37d 9h 25m | 2024-05-30 09:39 | 28 | Closed | Online | 2.072
93 | Causeway Point | Level 3 | AHU049 | Operation | Sensor | AHU | 30 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-05-31 09:39 | 16d 8h 55m | 2024-05-31 09:39 | 20 | Closed | Online | 1.48
94 | Causeway Point | Level 3 | Sensor 39 | Operation | Sensor | AHU | 1 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-06-01 09:39 | 1d 22h 50m | 2024-06-01 09:39 | 5 | Closed | Online | 0.37
95 | Causeway Point | Level 4 | Sensor 40 | Operation | Sensor | AHU | 2 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-06-02 09:39 | 5d 3h 50m | 2024-06-02 09:39 | 30 | Closed | Online | 2.22
96 | Causeway Point | Level 4 | Sensor 41 | Operation | Sensor | AHU | 40 | CHW CV not modulating (Out of Range/Stucked) | 2024-06-03 09:39 | 1d 2h 50m | 2024-06-03 09:39 | 0 | Closed | Online | 0
97 | Causeway Point | Level 1 | Sensor 17 | Operation | Sensor | AHU | 3 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-06-04 09:39 | 7d 22h 50m | 2024-06-04 09:39 | 0 | Closed | Online | 0
98 | Causeway Point | Level 1 | AHU050 | Operation | Sensor | AHU | 8 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-06-05 09:39 | 6d 28h 2m | 2024-06-05 09:39 | 35 | Closed | Online | 2.59
99 | Causeway Point | Level 3 | AHU051 | Operation | Sensor | AHU | 1 | Fault Static Pressure Sensor | 2024-06-06 09:39 | 3d 18h 30m | 2024-06-06 09:39 | 23 | Closed | Online | 1.702
100 | Causeway Point | Level 3 | AHU052 | Operation | Service | AHU | 3 | AHU VSD is not modulating | 2024-06-07 09:39 | 13d 16h 45m | 2024-06-07 09:39 | 0 | Closed | Online | 0
101 | Causeway Point | Level 1 | AHU053 | Operation | Service | AHU | 5 | Air Damper is not modulating | 2024-06-08 09:39 | 2h 10m | 2024-06-08 09:39 | 0 | In-Progress | Online | 0
102 | Causeway Point | Level 3 | Sensor 42 | Operation | Service | AHU | 2 | AHU is operating outside operation | 2024-06-09 09:39 | 7d 14h 25m | 2024-06-09 09:39 | 56 | Open | Offline | 4.144
103 | Causeway Point | Level 4 | Sensor 43 | Operation | Service | CH | 1 | AHU high VSD Speed (Default >40Hz User defined) | 2024-06-10 09:39 | 12d 23h 20m | 2024-06-10 09:39 | 0 | In-Progress | Online | 0
104 | Causeway Point | Level 3 | Sensor 44 | Operation | Service | CH | 2 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-06-11 09:39 | 7d 14h 25m | 2024-06-11 09:39 | 69 | In-Progress | Online | 5.106
105 | Causeway Point | Level 3 | Sensor 18 | Operation | Control | CH | 5 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-06-12 09:39 | 6d 0h 35m | 2024-06-12 09:39 | 100 | In-Progress | Online | 7.4
106 | Causeway Point | Level 3 | AHU054 | Operation | Control | CHWP | 6 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-06-13 09:39 | 37d 9h 25m | 2024-06-13 09:39 | 35 | In-Progress | Online | 2.59
107 | Causeway Point | Level 3 | AHU055 | Operation | Control | CHWP | 8 | CHW CV not modulating (Out of Range/Stucked) | 2024-06-14 09:39 | 16d 8h 55m | 2024-06-14 09:39 | 7 | In-Progress | Online | 0.518
108 | Causeway Point | Level 3 | AHU056 | Operation | Control | CHWP | 20 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-06-15 09:39 | 1d 22h 50m | 2024-06-15 09:39 | 60 | Closed | Online | 4.44
109 | Causeway Point | Level 4 | AHU057 | Operation | Control | CHWP | 15 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-06-16 09:39 | 5d 3h 50m | 2024-06-16 09:39 | 0 | Closed | Online | 0
110 | Causeway Point | Level 3 | Sensor 45 | Operation | Control | CHPL | 5 | Fault Static Pressure Sensor | 2024-06-17 09:39 | 1d 2h 50m | 2024-06-17 09:39 | 120 | Open | Online | 8.88
111 | Causeway Point | Level 4 | Sensor 46 | Operation | Control | CHPL | 4 | AHU VSD is not modulating | 2024-06-18 09:39 | 7d 22h 50m | 2024-06-18 09:39 | 0 | Open | Online | 0
112 | Causeway Point | Level 3 | Sensor 47 | Operation | Control | CT | 5 | Air Damper is not modulating | 2024-06-19 09:39 | 6d 28h 2m | 2024-06-19 09:39 | 0 | In-Progress | Online | 0
113 | Causeway Point | Level 3 | Sensor 19 | Operation | Control | CT | 16 | AHU is operating outside operation | 2024-06-20 09:39 | 3d 18h 30m | 2024-06-20 09:39 | 0 | In-Progress | Online | 0
114 | Causeway Point | Level 4 | AHU058 | Operation | Control | CT | 20 | AHU high VSD Speed (Default >40Hz User defined) | 2024-06-21 09:39 | 13d 16h 45m | 2024-06-21 09:39 | 0 | In-Progress | Online | 0
115 | Causeway Point | Level 4 | AHU059 | Operation | Control | CT | 2 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-06-22 09:39 | 2h 10m | 2024-06-22 09:39 | 0 | Closed | Offline | 0
116 | Causeway Point | Level 1 | AHU060 | Operation | Control | CT | 3 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-06-23 09:39 | 7d 14h 25m | 2024-06-23 09:39 | 62.1 | Closed | Online | 4.5954
117 | Causeway Point | Level 4 | AHU061 | Operation | Control | CT | 1 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-06-24 09:39 | 12d 23h 20m | 2024-06-24 09:39 | 0 | Closed | Online | 0
118 | Causeway Point | Level 1 | Sensor 48 | Operation | Control | CT | 25 | CHW CV not modulating (Out of Range/Stucked) | 2024-06-25 09:39 | 7d 14h 25m | 2024-06-25 09:39 | 0 | Closed | Online | 0
119 | Causeway Point | Level 3 | Sensor 49 | Operation | Control | CWP | 7 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-06-26 09:39 | 6d 0h 35m | 2024-06-26 09:39 | 0 | Closed | Online | 0
120 | Causeway Point | Level 5 | Sensor 50 | Operation | Control | CHWP | 8 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-06-27 09:39 | 37d 9h 25m | 2024-06-27 09:39 | 21.5 | Closed | Online | 1.591
121 | Causeway Point | Level 5 | Sensor 20 | Operation | Control | CHWP | 30 | Fault Static Pressure Sensor | 2024-06-28 09:39 | 16d 8h 55m | 2024-06-28 09:39 | 2 | Closed | Online | 0.148
122 | Causeway Point | Level 1 | AHU062 | Operation | Control | CHPL | 1 | AHU VSD is not modulating | 2024-06-29 09:39 | 1d 22h 50m | 2024-06-29 09:39 | 0 | Closed | Online | 0
123 | Causeway Point | Level 4 | AHU063 | Operation | Control | CHPL | 2 | Air Damper is not modulating | 2024-06-30 09:39 | 5d 3h 50m | 2024-06-30 09:39 | 0 | Closed | Online | 0
124 | Causeway Point | Level 5 | AHU064 | Operation | Control | CT | 40 | AHU is operating outside operation | 2024-07-01 09:39 | 1d 2h 50m | 2024-07-01 09:39 | 0 | Closed | Online | 0
125 | Causeway Point | Level 4 | AHU065 | Operation | Control | CT | 3 | AHU high VSD Speed (Default >40Hz User defined) | 2024-07-02 09:39 | 7d 22h 50m | 2024-07-02 09:39 | 0 | Closed | Online | 0
126 | Causeway Point | Level 4 | Sensor 51 | Operation | Control | CT | 8 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-07-03 09:39 | 6d 28h 2m | 2024-07-03 09:39 | 0 | Closed | Online | 0
127 | Causeway Point | Level 4 | Sensor 52 | Operation | Control | CT | 1 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-07-04 09:39 | 3d 18h 30m | 2024-07-04 09:39 | 21.6 | Closed | Online | 1.5984
128 | Causeway Point | Level 3 | Sensor 53 | Operation | Control | CT | 3 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-07-05 09:39 | 13d 16h 45m | 2024-07-05 09:39 | 3 | Closed | Offline | 0.222
129 | Causeway Point | Level 1 | Sensor 21 | Operation | Control | CT | 5 | CHW CV not modulating (Out of Range/Stucked) | 2024-07-06 09:39 | 2h 10m | 2024-07-06 09:39 | 0 | Closed | Online | 0
130 | Hougang Mall | Level 2 | AHU066 | Operation | Control | CT | 2 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-07-07 09:39 | 7d 14h 25m | 2024-07-07 09:39 | 0 | Closed | Online | 0
131 | Hougang Mall | Level 4 | AHU067 | Operation | Control | CWP | 1 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-07-08 09:39 | 12d 23h 20m | 2024-07-08 09:39 | 0 | Closed | Online | 0
132 | Hougang Mall | Level B1 | AHU068 | Operation | Control | CWP | 2 | Fault Static Pressure Sensor | 2024-07-09 09:39 | 7d 14h 25m | 2024-07-09 09:39 | 0 | Closed | Online | 0
133 | Hougang Mall | Level B1 | AHU069 | Operation | Control | CWP | 5 | AHU VSD is not modulating | 2024-07-10 09:39 | 6d 0h 35m | 2024-07-10 09:39 | 35.5 | Closed | Online | 2.627
134 | Hougang Mall | Level 3 | Sensor 54 | Operation | Control | AHU | 6 | Air Damper is not modulating | 2024-07-11 09:39 | 37d 9h 25m | 2024-07-11 09:39 | 620 | Closed | Online | 45.88
135 | Hougang Mall | Level 1 | Sensor 55 | Operation | Control | AHU | 8 | AHU is operating outside operation | 2024-07-12 09:39 | 16d 8h 55m | 2024-07-12 09:39 | 28 | Closed | Online | 2.072
136 | Hougang Mall | Level 3 | Sensor 56 | Operation | Control | AHU | 20 | AHU high VSD Speed (Default >40Hz User defined) | 2024-07-13 09:39 | 1d 22h 50m | 2024-07-13 09:39 | 20 | Closed | Online | 1.48
137 | Hougang Mall | Level 2 | Sensor 22 | Operation | Control | AHU | 15 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-07-14 09:39 | 5d 3h 50m | 2024-07-14 09:39 | 5 | Closed | Online | 0.37
138 | Hougang Mall | Level B2 | AHU070 | Operation | Control | AHU | 5 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-07-15 09:39 | 1d 2h 50m | 2024-07-15 09:39 | 30 | Closed | Online | 2.22
139 | Hougang Mall | Level 3 | AHU071 | Operation | Control | AHU | 4 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-07-16 09:39 | 7d 22h 50m | 2024-07-16 09:39 | 0 | Closed | Online | 0
140 | Hougang Mall | Level 4 | AHU072 | Operation | Control | AHU | 5 | CHW CV not modulating (Out of Range/Stucked) | 2024-07-17 09:39 | 6d 28h 2m | 2024-07-17 09:39 | 0 | Closed | Online | 0
141 | Hougang Mall | Level 1 | AHU073 | Operation | Control | AHU | 16 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-07-18 09:39 | 3d 18h 30m | 2024-07-18 09:39 | 35 | Closed | Offline | 2.59
142 | Hougang Mall | Level 3 | Sensor 57 | Operation | Control | AHU | 20 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-07-19 09:39 | 13d 16h 45m | 2024-07-19 09:39 | 23 | Closed | Online | 1.702
143 | Hougang Mall | Level 4 | Sensor 58 | Operation | Control | AHU | 2 | Fault Static Pressure Sensor | 2024-07-20 09:39 | 2h 10m | 2024-07-20 09:39 | 0 | In-Progress | Online | 0
144 | Hougang Mall | Level 4 | Sensor 59 | Operation | Control | AHU | 3 | AHU VSD is not modulating | 2024-07-21 09:39 | 7d 14h 25m | 2024-07-21 09:39 | 0 | In-Progress | Online | 0
145 | Hougang Mall | Level 1 | Sensor 23 | Operation | Control | AHU | 1 | Air Damper is not modulating | 2024-07-22 09:39 | 12d 23h 20m | 2024-07-22 09:39 | 56 | Open | Online | 4.144
146 | Hougang Mall | Level 3 | AHU074 | Operation | Control | AHU | 25 | AHU is operating outside operation | 2024-07-23 09:39 | 7d 14h 25m | 2024-07-23 09:39 | 0 | Open | Online | 0
147 | Hougang Mall | Level 4 | AHU075 | Operation | Control | AHU | 7 | AHU high VSD Speed (Default >40Hz User defined) | 2024-07-24 09:39 | 6d 0h 35m | 2024-07-24 09:39 | 69 | In-Progress | Online | 5.106
148 | Hougang Mall | Level 4 | AHU076 | Operation | Control | AHU | 1 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-07-25 09:39 | 37d 9h 25m | 2024-07-25 09:39 | 100 | Closed | Online | 7.4
149 | Hougang Mall | Level 1 | AHU077 | Operation | Control | CH | 3 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-07-26 09:39 | 16d 8h 55m | 2024-07-26 09:39 | 35 | Closed | Online | 2.59
150 | Hougang Mall | Level 5 | Sensor 60 | Operation | Control | CH | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-07-27 09:39 | 1d 22h 50m | 2024-07-27 09:39 | 7 | Closed | Online | 0.518
151 | Hougang Mall | Level 3 | Sensor 61 | Operation | Control | CH | 2 | CHW CV not modulating (Out of Range/Stucked) | 2024-07-28 09:39 | 5d 3h 50m | 2024-07-28 09:39 | 60 | Closed | Online | 4.44
152 | North Point City (North Wing) | Level 4 | Sensor 62 | Operation | Control | CHWP | 1 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-07-29 09:39 | 1d 2h 50m | 2024-07-29 09:39 | 0 | Closed | Online | 0
153 | North Point City (North Wing) | Level B1 | Sensor 24 | Operation | Sensor | CHWP | 2 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-07-30 09:39 | 7d 22h 50m | 2024-07-30 09:39 | 120 | Closed | Online | 8.88
154 | North Point City (North Wing) | Level 3 | AHU078 | Operation | Sensor | CHWP | 5 | Fault Static Pressure Sensor | 2024-07-31 09:39 | 6d 28h 2m | 2024-07-31 09:39 | 0 | Closed | Offline | 0
155 | North Point City (North Wing) | Level 3 | AHU079 | Operation | Sensor | CHWP | 6 | AHU VSD is not modulating | 2024-08-01 09:39 | 3d 18h 30m | 2024-08-01 09:39 | 0 | Closed | Offline | 0
156 | North Point City (North Wing) | Level 4 | AHU080 | Operation | Sensor | CHPL | 8 | Air Damper is not modulating | 2024-08-02 09:39 | 13d 16h 45m | 2024-08-02 09:39 | 0 | Closed | Online | 0
157 | North Point City (South Wing) | Level 3 | AHU081 | Operation | Sensor | CHPL | 20 | AHU is operating outside operation | 2024-08-03 09:39 | 2h 10m | 2024-08-03 09:39 | 0 | Closed | Offline | 0
158 | North Point City (South Wing) | Level 4 | Sensor 63 | Operation | Sensor | CT | 15 | AHU high VSD Speed (Default >40Hz User defined) | 2024-08-04 09:39 | 7d 14h 25m | 2024-08-04 09:39 | 0 | Closed | Online | 0
159 | North Point City (North Wing) | Level 1 | Sensor 64 | Operation | Sensor | CT | 5 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-08-05 09:39 | 12d 23h 20m | 2024-08-05 09:39 | 62.1 | Closed | Offline | 4.5954
160 | North Point City (North Wing) | Level 3 | Sensor 65 | Operation | Sensor | CT | 4 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-08-06 09:39 | 7d 14h 25m | 2024-08-06 09:39 | 0 | Closed | Online | 0
161 | North Point City (North Wing) | Level 3 | Sensor 25 | Operation | Sensor | CT | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-08-07 09:39 | 6d 0h 35m | 2024-08-07 09:39 | 0 | Closed | Offline | 0
162 | North Point City (North Wing) | Level 3 | AHU082 | Operation | Sensor | CT | 16 | CHW CV not modulating (Out of Range/Stucked) | 2024-08-08 09:39 | 37d 9h 25m | 2024-08-08 09:39 | 0 | Closed | Online | 0
163 | North Point City (North Wing) | Level 4 | AHU083 | Operation | Sensor | CT | 20 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-08-09 09:39 | 16d 8h 55m | 2024-08-09 09:39 | 21.5 | Closed | Online | 1.591
164 | North Point City (North Wing) | Level 4 | AHU084 | Operation | Service | CT | 2 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-08-10 09:39 | 1d 22h 50m | 2024-08-10 09:39 | 2 | Closed | Online | 0.148
165 | North Point City (South Wing) | Level 3 | AHU085 | Operation | Service | CWP | 3 | Fault Static Pressure Sensor | 2024-08-11 09:39 | 5d 3h 50m | 2024-08-11 09:39 | 0 | Closed | Online | 0
166 | North Point City (South Wing) | Level 3 | Sensor 66 | Operation | Service | CHWP | 1 | AHU VSD is not modulating | 2024-08-12 09:39 | 1d 2h 50m | 2024-08-12 09:39 | 0 | Open | Online | 0
167 | North Point City (South Wing) | Level 1 | Sensor 67 | Operation | Service | CHWP | 25 | Air Damper is not modulating | 2024-08-13 09:39 | 7d 22h 50m | 2024-08-13 09:39 | 0 | In-Progress | Online | 0
168 | North Point City (South Wing) | Level 1 | Sensor 68 | Operation | Service | CHPL | 7 | AHU is operating outside operation | 2024-08-14 09:39 | 6d 28h 2m | 2024-08-14 09:39 | 0 | In-Progress | Online | 0
169 | North Point City (South Wing) | Level 3 | Sensor 26 | Operation | Control | CHPL | 8 | AHU high VSD Speed (Default >40Hz User defined) | 2024-08-15 09:39 | 3d 18h 30m | 2024-08-15 09:39 | 0 | In-Progress | Online | 0
170 | North Point City (North Wing) | Level 1 | AHU086 | Operation | Control | CT | 30 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-08-16 09:39 | 13d 16h 45m | 2024-08-16 09:39 | 21.6 | Closed | Online | 1.5984
171 | North Point City (North Wing) | Level 1 | AHU087 | Operation | Control | CT | 1 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-08-18 09:39 | 2h 10m | 2023-08-18 09:39 | 3 | Closed | Online | 0.222
172 | North Point City (South Wing) | Level 5 | AHU088 | Operation | Control | CT | 2 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-08-19 09:39 | 7d 14h 25m | 2023-08-19 09:39 | 0 | Closed | Online | 0
173 | North Point City (South Wing) | Level 5 | AHU089 | Operation | Control | CT | 40 | CHW CV not modulating (Out of Range/Stucked) | 2023-08-20 09:39 | 12d 23h 20m | 2023-08-20 09:39 | 0 | Closed | Offline | 0
174 | Tampines 1 | Level B1 | Sensor 69 | Operation | Control | CT | 3 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-08-21 09:39 | 7d 14h 25m | 2023-08-21 09:39 | 0 | Closed | Offline | 0
175 | Tampines 1 | Level 4 | Sensor 70 | Operation | Control | CT | 8 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-08-22 09:39 | 6d 0h 35m | 2023-08-22 09:39 | 0 | Closed | Offline | 0
176 | Tampines 1 | Level 3 | Sensor 71 | Operation | Control | CT | 1 | AHU VSD is not modulating | 2023-08-23 09:39 | 37d 9h 25m | 2023-08-23 09:39 | 35.5 | Closed | Online | 2.627
177 | Tampines 1 | Level 4 | Sensor 27 | Operation | Control | CWP | 3 | Air Damper is not modulating | 2023-08-24 09:39 | 16d 8h 55m | 2023-08-24 09:39 | 620 | Closed | Online | 45.88
178 | Tampines 1 | Level 4 | AHU090 | Operation | Control | CWP | 5 | AHU is operating outside operation | 2023-08-25 09:39 | 1d 22h 50m | 2023-08-25 09:39 | 28 | Closed | Online | 2.072
179 | Tampines 1 | Level 1 | AHU091 | Operation | Control | CWP | 2 | AHU high VSD Speed (Default >40Hz User defined) | 2023-08-26 09:39 | 5d 3h 50m | 2023-08-26 09:39 | 20 | Closed | Online | 1.48
180 | Tampines 1 | Level B1 | AHU092 | Operation | Control | AHU | 1 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-08-27 09:39 | 1d 2h 50m | 2023-08-27 09:39 | 5 | Closed | Online | 0.37
181 | Tampines 1 | Level 3 | AHU093 | Operation | Control | AHU | 2 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-08-28 09:39 | 7d 22h 50m | 2023-08-28 09:39 | 30 | Closed | Online | 2.22
182 | Tampines 1 | Level 2 | Sensor 72 | Operation | Control | AHU | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-08-29 09:39 | 6d 28h 2m | 2023-08-29 09:39 | 0 | Closed | Online | 0
183 | Tampines 1 | Level 1 | Sensor 73 | Operation | Control | AHU | 8 | CHW CV not modulating (Out of Range/Stucked) | 2023-08-30 09:39 | 3d 18h 30m | 2023-08-30 09:39 | 0 | Closed | Online | 0
184 | Tampines 1 | Level 2 | Sensor 74 | Operation | Control | AHU | 30 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-08-31 09:39 | 13d 16h 45m | 2023-08-31 09:39 | 35 | Closed | Online | 2.59
185 | Tampines 1 | Level B1 | Sensor 28 | Operation | Control | AHU | 1 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-09-01 09:39 | 2h 10m | 2023-09-01 09:39 | 23 | Closed | Online | 1.702
186 | Tampines 1 | Level 2 | AHU094 | Operation | Control | AHU | 2 | Fault Static Pressure Sensor | 2023-09-02 09:39 | 7d 14h 25m | 2023-09-02 09:39 | 0 | Closed | Online | 0
187 | Tampines 1 | Level B1 | AHU095 | Operation | Control | AHU | 40 | AHU VSD is not modulating | 2023-09-03 09:39 | 12d 23h 20m | 2023-09-03 09:39 | 0 | Closed | Online | 0
188 | Tampines 1 | Level 4 | AHU096 | Operation | Control | AHU | 3 | Air Damper is not modulating | 2023-09-04 09:39 | 7d 14h 25m | 2023-09-04 09:39 | 56 | Closed | Online | 4.144
189 | Tampines 1 | Level 2 | AHU097 | Operation | Control | AHU | 8 | AHU is operating outside operation | 2023-09-05 09:39 | 6d 0h 35m | 2023-09-05 09:39 | 0 | Closed | Offline | 0
190 | Tampines 1 | Level B1 | Sensor 75 | Operation | Control | AHU | 1 | AHU high VSD Speed (Default >40Hz User defined) | 2023-09-06 09:39 | 37d 9h 25m | 2023-09-06 09:39 | 69 | Closed | Offline | 5.106
191 | Tampines 1 | Level 2 | Sensor 76 | Operation | Control | AHU | 3 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-09-07 09:39 | 16d 8h 55m | 2023-09-07 09:39 | 100 | Closed | Online | 7.4
192 | Tampines 1 | Level 3 | Sensor 77 | Operation | Control | AHU | 5 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-09-08 09:39 | 1d 22h 50m | 2023-09-08 09:39 | 35 | Closed | Online | 2.59
193 | Tampines 1 | Level 3 | Sensor 29 | Operation | Control | AHU | 2 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-09-09 09:39 | 5d 3h 50m | 2023-09-09 09:39 | 7 | Closed | Online | 0.518
194 | Tampines 1 | Level 4 | AHU098 | Operation | Control | AHU | 1 | CHW CV not modulating (Out of Range/Stucked) | 2023-09-10 09:39 | 1d 2h 50m | 2023-09-10 09:39 | 60 | Closed | Online | 4.44
195 | Tampines 1 | Level 3 | AHU099 | Operation | Control | CH | 2 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-09-11 09:39 | 7d 22h 50m | 2023-09-11 09:39 | 0 | Closed | Online | 0
196 | Tampines 1 | Level 4 | AHU100 | Operation | Control | CH | 5 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-09-12 09:39 | 6d 28h 2m | 2023-09-12 09:39 | 120 | Closed | Online | 8.88
197 | Tampines 1 | Level 2 | AHU101 | Operation | Control | CH | 6 | Fault Static Pressure Sensor | 2023-09-13 09:39 | 3d 18h 30m | 2023-09-13 09:39 | 0 | Closed | Online | 0
198 | Tampines 1 | Level B1 | Sensor 78 | Operation | Control | CHWP | 8 | AHU VSD is not modulating | 2023-09-14 09:39 | 13d 16h 45m | 2023-09-14 09:39 | 0 | Closed | Online | 0
199 | Tampines 1 | Level 3 | Sensor 79 | Operation | Control | CHWP | 20 | Air Damper is not modulating | 2023-09-15 09:39 | 2h 10m | 2023-09-15 09:39 | 0 | Closed | Online | 0
200 | Tampines 1 | Level 3 | Sensor 80 | Operation | Control | CHWP | 15 | AHU is operating outside operation | 2023-09-16 09:39 | 7d 14h 25m | 2023-09-16 09:39 | 0 | Closed | Online | 0
201 | Tampines 1 | Level B1 | Sensor 30 | Operation | Control | CHWP | 5 | AHU high VSD Speed (Default >40Hz User defined) | 2023-09-17 09:39 | 12d 23h 20m | 2023-09-17 09:39 | 0 | Closed | Online | 0
202 | Tampines 1 | Level 2 | AHU102 | Operation | Control | CHPL | 4 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-09-18 09:39 | 7d 14h 25m | 2023-09-18 09:39 | 62.1 | Closed | Online | 4.5954
203 | Tampines 1 | Level 3 | AHU103 | Operation | Control | CHPL | 5 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-09-19 09:39 | 6d 0h 35m | 2023-09-19 09:39 | 0 | Closed | Offline | 0
204 | Tampines 1 | Level 4 | AHU104 | Operation | Control | CT | 16 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-09-20 09:39 | 37d 9h 25m | 2023-09-20 09:39 | 0 | Closed | Online | 0
205 | Tampines 1 | Level B1 | AHU105 | Operation | Control | CT | 20 | CHW CV not modulating (Out of Range/Stucked) | 2023-09-21 09:39 | 16d 8h 55m | 2023-09-21 09:39 | 0 | Closed | Online | 0
206 | Tampines 1 | Level 3 | Sensor 81 | Operation | Control | CT | 2 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-09-22 09:39 | 1d 22h 50m | 2023-09-22 09:39 | 21.5 | Closed | Online | 1.591
207 | Tampines 1 | Level 2 | Sensor 82 | Operation | Control | CT | 3 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-09-23 09:39 | 5d 3h 50m | 2023-09-23 09:39 | 2 | Closed | Online | 0.148
208 | Tampines 1 | Level 3 | Sensor 83 | Operation | Control | CT | 1 | Fault Static Pressure Sensor | 2023-09-24 09:39 | 1d 2h 50m | 2023-09-24 09:39 | 0 | Closed | Online | 0
209 | Tampines 1 | Level 4 | Sensor 31 | Operation | Control | CT | 25 | AHU VSD is not modulating | 2023-09-25 09:39 | 7d 22h 50m | 2023-09-25 09:39 | 0 | Closed | Online | 0
210 | Tampines 1 | Level 4 | AHU106 | Operation | Control | CT | 7 | Air Damper is not modulating | 2023-09-26 09:39 | 6d 28h 2m | 2023-09-26 09:39 | 0 | Closed | Online | 0
211 | Tampines 1 | Level B1 | AHU107 | Operation | Control | CWP | 8 | AHU is operating outside operation | 2023-09-27 09:39 | 3d 18h 30m | 2023-09-27 09:39 | 0 | Closed | Online | 0
212 | Tampines 1 | Level 4 | AHU108 | Operation | Control | CHWP | 30 | AHU high VSD Speed (Default >40Hz User defined) | 2023-09-28 09:39 | 13d 16h 45m | 2023-09-28 09:39 | 0 | Closed | Online | 0
213 | Tampines 1 | Level B1 | AHU109 | Operation | Control | CHWP | 1 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-09-29 09:39 | 2h 10m | 2023-09-29 09:39 | 21.6 | Closed | Online | 1.5984
214 | Tampines 1 | Level 3 | Sensor 84 | Operation | Control | CHPL | 2 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-09-30 09:39 | 7d 14h 25m | 2023-09-30 09:39 | 3 | Closed | Online | 0.222
215 | Tampines 1 | Level 3 | Sensor 85 | Operation | Control | CHPL | 40 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-10-01 09:39 | 12d 23h 20m | 2023-10-01 09:39 | 0 | Closed | Online | 0
216 | Tampines 1 | Level 3 | Sensor 86 | Operation | Control | CT | 3 | CHW CV not modulating (Out of Range/Stucked) | 2023-10-02 09:39 | 7d 14h 25m | 2023-10-02 09:39 | 0 | Closed | Offline | 0
217 | Tampines 1 | Level 1 | Sensor 32 | Operation | Sensor | CT | 8 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-10-03 09:39 | 6d 0h 35m | 2023-10-03 09:39 | 0 | Closed | Online | 0
218 | Tampines 1 | Level 1 | AHU110 | Operation | Sensor | CT | 1 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-10-04 09:39 | 37d 9h 25m | 2023-10-04 09:39 | 0 | Closed | Online | 0
219 | Tampines 1 | Level 3 | AHU111 | Operation | Sensor | CT | 3 | Fault Static Pressure Sensor | 2023-10-05 09:39 | 16d 8h 55m | 2023-10-05 09:39 | 35.5 | Closed | Online | 2.627
220 | Tampines 1 | Level 4 | AHU112 | Operation | Sensor | CT | 5 | AHU VSD is not modulating | 2023-10-06 09:39 | 1d 22h 50m | 2023-10-06 09:39 | 620 | Open | Online | 45.88
221 | Tampines 1 | Level 3 | AHU113 | Operation | Sensor | CT | 2 | Air Damper is not modulating | 2023-10-07 09:39 | 5d 3h 50m | 2023-10-07 09:39 | 28 | In-Progress | Online | 2.072
222 | Tampines 1 | Level 4 | Sensor 87 | Operation | Sensor | CT | 1 | AHU is operating outside operation | 2023-10-08 09:39 | 1d 2h 50m | 2023-10-08 09:39 | 20 | In-Progress | Online | 1.48
223 | Tampines 1 | Level 3 | Sensor 88 | Operation | Sensor | CWP | 2 | AHU high VSD Speed (Default >40Hz User defined) | 2023-10-09 09:39 | 7d 22h 50m | 2023-10-09 09:39 | 5 | In-Progress | Online | 0.37
224 | Tampines 1 | Level 1 | Sensor 89 | Operation | Sensor | CWP | 5 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-10-10 09:39 | 6d 28h 2m | 2023-10-10 09:39 | 30 | Open | Online | 2.22
225 | Tampines 1 | Level 3 | Sensor 33 | Operation | Sensor | CWP | 6 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-10-11 09:39 | 3d 18h 30m | 2023-10-11 09:39 | 0 | Open | Online | 0
226 | Tampines 1 | Level 3 | AHU114 | Operation | Sensor | AHU | 8 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-10-12 09:39 | 13d 16h 45m | 2023-10-12 09:39 | 0 | Open | Online | 0
227 | Tampines 1 | Level 4 | AHU115 | Operation | Sensor | AHU | 20 | CHW CV not modulating (Out of Range/Stucked) | 2023-10-13 09:39 | 2h 10m | 2023-10-13 09:39 | 35 | In-Progress | Online | 2.59
228 | Tampines 1 | Level 3 | AHU116 | Operation | Service | AHU | 15 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-10-14 09:39 | 7d 14h 25m | 2023-10-14 09:39 | 23 | In-Progress | Online | 1.702
229 | Tampines 1 | Level 3 | AHU117 | Operation | Service | AHU | 5 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-10-15 09:39 | 12d 23h 20m | 2023-10-15 09:39 | 0 | In-Progress | Offline | 0
230 | Tampines 1 | Level 4 | Sensor 90 | Operation | Service | AHU | 4 | Fault Static Pressure Sensor | 2023-10-16 09:39 | 7d 14h 25m | 2023-10-16 09:39 | 0 | In-Progress | Online | 0
231 | Tampines 1 | Level 1 | Sensor 91 | Operation | Service | AHU | 5 | AHU VSD is not modulating | 2023-10-17 09:39 | 6d 0h 35m | 2023-10-17 09:39 | 56 | In-Progress | Online | 4.144
232 | Tampines 1 | Level 1 | Sensor 92 | Operation | Service | AHU | 16 | Air Damper is not modulating | 2023-10-18 09:39 | 37d 9h 25m | 2023-10-18 09:39 | 0 | In-Progress | Online | 0
233 | Tampines 1 | Level B2 | Sensor 34 | Operation | Control | AHU | 20 | AHU is operating outside operation | 2023-10-19 09:39 | 16d 8h 55m | 2023-10-19 09:39 | 69 | In-Progress | Online | 5.106
234 | Tampines 1 | Level 1 | AHU118 | Operation | Control | AHU | 2 | AHU high VSD Speed (Default >40Hz User defined) | 2023-10-20 09:39 | 1d 22h 50m | 2023-10-20 09:39 | 100 | Closed | Online | 7.4
235 | Tampines 1 | Level 3 | AHU119 | Operation | Control | AHU | 3 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-10-21 09:39 | 5d 3h 50m | 2023-10-21 09:39 | 35 | Closed | Online | 2.59
236 | Tampines 1 | Level 3 | AHU120 | Operation | Control | AHU | 1 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-10-22 09:39 | 1d 2h 50m | 2023-10-22 09:39 | 7 | Closed | Online | 0.518
237 | Tampines 1 | Level 4 | AHU121 | Operation | Control | AHU | 25 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-10-23 09:39 | 7d 22h 50m | 2023-10-23 09:39 | 60 | In-Progress | Online | 4.44
238 | Tampines 1 | Level 1 | Sensor 93 | Operation | Control | AHU | 7 | CHW CV not modulating (Out of Range/Stucked) | 2023-10-24 09:39 | 6d 28h 2m | 2023-10-24 09:39 | 0 | In-Progress | Online | 0
239 | Tampines 1 | Level 3 | Sensor 94 | Operation | Control | AHU | 1 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-10-25 09:39 | 3d 18h 30m | 2023-10-25 09:39 | 120 | Closed | Online | 8.88
240 | Tampines 1 | Level 3 | Sensor 95 | Operation | Control | AHU | 3 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-10-26 09:39 | 13d 16h 45m | 2023-10-26 09:39 | 0 | Closed | Online | 0
241 | Tampines 1 | Level 3 | Sensor 35 | Operation | Control | CH | 5 | Fault Static Pressure Sensor | 2023-10-27 09:39 | 2h 10m | 2023-10-27 09:39 | 0 | Closed | Online | 0
242 | Tampines 1 | Level 4 | AHU122 | Energy | Control | CH | 2 | AHU VSD is not modulating | 2023-10-28 09:39 | 7d 14h 25m | 2023-10-28 09:39 | 0 | Closed | Offline | 0
243 | Tampines 1 | Level 4 | AHU123 | Energy | Control | CH | 1 | Air Damper is not modulating | 2023-10-29 09:39 | 12d 23h 20m | 2023-10-29 09:39 | 0 | Closed | Online | 0
244 | Tampines 1 | Level 4 | AHU124 | Energy | Control | CHWP | 2 | AHU is operating outside operation | 2023-10-30 09:39 | 7d 14h 25m | 2023-10-30 09:39 | 0 | Closed | Online | 0
245 | Tampines 1 | Level 3 | AHU125 | Energy | Control | CHWP | 5 | AHU high VSD Speed (Default >40Hz User defined) | 2023-10-31 09:39 | 6d 0h 35m | 2023-10-31 09:39 | 62.1 | Closed | Online | 4.5954
246 | Tampines 1 | Level B2 | Sensor 96 | Energy | Control | CHWP | 6 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-11-01 09:39 | 37d 9h 25m | 2023-11-01 09:39 | 0 | Closed | Online | 0
247 | Tampines 1 | Level 1 | Sensor 97 | Energy | Control | CHWP | 8 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-11-02 09:39 | 16d 8h 55m | 2023-11-02 09:39 | 0 | Closed | Online | 0
248 | Tampines 1 | Level 5 | Sensor 98 | Energy | Control | CHPL | 20 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-11-03 09:39 | 1d 22h 50m | 2023-11-03 09:39 | 0 | Closed | Online | 0
249 | Tampines 1 | Level 5 | Sensor 36 | Energy | Control | CHPL | 15 | CHW CV not modulating (Out of Range/Stucked) | 2023-11-04 09:39 | 5d 3h 50m | 2023-11-04 09:39 | 21.5 | Closed | Online | 1.591
250 | Tampines 1 | Level 5 | AHU126 | Energy | Control | CT | 5 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-11-05 09:39 | 1d 2h 50m | 2023-11-05 09:39 | 2 | Closed | Online | 0.148
251 | Tampines 1 | Level 1 | AHU127 | Energy | Control | CT | 4 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-11-06 09:39 | 7d 22h 50m | 2023-11-06 09:39 | 0 | Closed | Online | 0
252 | Tampines 1 | Level 4 | AHU128 | Energy | Control | CT | 5 | Fault Static Pressure Sensor | 2023-11-07 09:39 | 6d 28h 2m | 2023-11-07 09:39 | 0 | Closed | Online | 0
253 | Tampines 1 | Level 5 | AHU129 | Energy | Control | CT | 16 | AHU VSD is not modulating | 2023-11-08 09:39 | 3d 18h 30m | 2023-11-08 09:39 | 0 | Closed | Online | 0
254 | Tampines 1 | Level 4 | Sensor 99 | Energy | Control | CT | 20 | Air Damper is not modulating | 2023-11-09 09:39 | 13d 16h 45m | 2023-11-09 09:39 | 0 | Closed | Online | 0
255 | Tampines 1 | Level 3 | Sensor 100 | Energy | Control | CT | 2 | AHU is operating outside operation | 2023-11-10 09:39 | 2h 10m | 2023-11-10 09:39 | 0 | Closed | Offline | 0
256 | Tampines 1 | Level 1 | Sensor 101 | Energy | Control | CT | 3 | AHU high VSD Speed (Default >40Hz User defined) | 2023-11-11 09:39 | 7d 14h 25m | 2023-11-11 09:39 | 21.6 | Closed | Online | 1.5984
257 | Tampines 1 | Level 5 | Sensor 37 | Energy | Control | CWP | 1 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-11-12 09:39 | 12d 23h 20m | 2023-11-12 09:39 | 3 | Closed | Online | 0.222
258 | Tampines 1 | Level 3 | AHU130 | Energy | Control | CHWP | 25 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-11-13 09:39 | 7d 14h 25m | 2023-11-13 09:39 | 0 | Closed | Online | 0
259 | Tampines 1 | Level 4 | AHU131 | Energy | Control | CHWP | 7 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-11-14 09:39 | 6d 0h 35m | 2023-11-14 09:39 | 0 | Closed | Online | 0
260 | The Centrepoint | Level 2 | AHU132 | Energy | Control | CHPL | 8 | CHW CV not modulating (Out of Range/Stucked) | 2023-11-15 09:39 | 37d 9h 25m | 2023-11-15 09:39 | 0 | Closed | Online | 0
261 | The Centrepoint | Level B2 | AHU133 | Energy | Control | CHPL | 30 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-11-16 09:39 | 16d 8h 55m | 2023-11-16 09:39 | 0 | Closed | Online | 0
262 | The Centrepoint | Level 4 | Sensor 102 | Energy | Control | CT | 1 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-11-17 09:39 | 1d 22h 50m | 2023-11-17 09:39 | 35.5 | Closed | Online | 2.627
263 | The Centrepoint | Level 3 | Sensor 103 | Energy | Control | CT | 2 | AHU VSD is not modulating | 2023-11-18 09:39 | 5d 3h 50m | 2023-11-18 09:39 | 620 | Closed | Online | 45.88
264 | The Centrepoint | Level B1 | Sensor 104 | Energy | Control | CT | 40 | Air Damper is not modulating | 2023-11-19 09:39 | 1d 2h 50m | 2023-11-19 09:39 | 28 | Closed | Online | 2.072
265 | The Centrepoint | Level 2 | Sensor 38 | Energy | Control | CT | 3 | AHU is operating outside operation | 2023-11-20 09:39 | 7d 22h 50m | 2023-11-20 09:39 | 20 | Closed | Online | 1.48
266 | The Centrepoint | Level 4 | AHU134 | Energy | Control | CT | 8 | AHU high VSD Speed (Default >40Hz User defined) | 2023-11-21 09:39 | 6d 28h 2m | 2023-11-21 09:39 | 5 | Closed | Online | 0.37
267 | The Centrepoint | Level 3 | AHU135 | Energy | Control | CT | 1 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-11-22 09:39 | 3d 18h 30m | 2023-11-22 09:39 | 30 | Closed | Online | 2.22
268 | The Centrepoint | Level 3 | AHU136 | Energy | Control | CT | 3 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-11-23 09:39 | 13d 16h 45m | 2023-11-23 09:39 | 0 | Closed | Offline | 0
269 | The Centrepoint | Level 4 | AHU137 | Energy | Control | CWP | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-11-24 09:39 | 2h 10m | 2023-11-24 09:39 | 0 | Closed | Online | 0
270 | The Centrepoint | Level 4 | Sensor 105 | Energy | Control | CWP | 2 | CHW CV not modulating (Out of Range/Stucked) | 2023-11-25 09:39 | 7d 14h 25m | 2023-11-25 09:39 | 35 | Closed | Online | 2.59
271 | The Centrepoint | Level B2 | Sensor 106 | Energy | Control | CWP | 1 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-11-26 09:39 | 12d 23h 20m | 2023-11-26 09:39 | 23 | Closed | Online | 1.702
272 | The Centrepoint | Level 4 | Sensor 107 | Energy | Control | AHU | 2 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-11-27 09:39 | 7d 14h 25m | 2023-11-27 09:39 | 0 | Closed | Online | 0
273 | The Centrepoint | Level 3 | Sensor 39 | Energy | Control | AHU | 5 | Fault Static Pressure Sensor | 2023-11-28 09:39 | 6d 0h 35m | 2023-11-28 09:39 | 0 | Closed | Online | 0
274 | The Centrepoint | Level B1 | AHU138 | Energy | Control | AHU | 8 | AHU VSD is not modulating | 2023-11-29 09:39 | 37d 9h 25m | 2023-11-29 09:39 | 56 | Closed | Online | 4.144
275 | The Centrepoint | Level 3 | AHU139 | Energy | Control | AHU | 30 | Air Damper is not modulating | 2023-11-30 09:39 | 16d 8h 55m | 2023-11-30 09:39 | 0 | Closed | Online | 0
276 | The Centrepoint | Level 2 | AHU140 | Energy | Control | AHU | 1 | AHU is operating outside operation | 2023-12-01 09:39 | 1d 22h 50m | 2023-12-01 09:39 | 69 | Closed | Online | 5.106
277 | The Centrepoint | Level 3 | AHU141 | Energy | Control | AHU | 2 | AHU high VSD Speed (Default >40Hz User defined) | 2023-12-02 09:39 | 5d 3h 50m | 2023-12-02 09:39 | 100 | Closed | Online | 7.4
278 | The Centrepoint | Level 1 | Sensor 108 | Energy | Control | AHU | 40 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-12-03 09:39 | 1d 2h 50m | 2023-12-03 09:39 | 35 | Closed | Online | 2.59
279 | The Centrepoint | Level 3 | Sensor 109 | Energy | Control | AHU | 3 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-12-04 09:39 | 7d 22h 50m | 2023-12-04 09:39 | 7 | Closed | Online | 0.518
280 | The Centrepoint | Level B1 | Sensor 110 | Energy | Control | AHU | 8 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-12-05 09:39 | 6d 28h 2m | 2023-12-05 09:39 | 60 | Closed | Online | 4.44
281 | The Centrepoint | Level 3 | Sensor 40 | Energy | Sensor | AHU | 1 | CHW CV not modulating (Out of Range/Stucked) | 2023-12-06 09:39 | 3d 18h 30m | 2023-12-06 09:39 | 0 | Closed | Offline | 0
282 | The Centrepoint | Level B1 | AHU142 | Energy | Sensor | AHU | 3 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-12-07 09:39 | 13d 16h 45m | 2023-12-07 09:39 | 120 | Closed | Online | 8.88
283 | The Centrepoint | Level 2 | AHU143 | Energy | Sensor | AHU | 5 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-12-08 09:39 | 2h 10m | 2023-12-08 09:39 | 0 | Closed | Online | 0
284 | The Centrepoint | Level B1 | AHU144 | Energy | Sensor | AHU | 2 | Fault Static Pressure Sensor | 2023-12-09 09:39 | 7d 14h 25m | 2023-12-09 09:39 | 0 | Closed | Online | 0
285 | The Centrepoint | Level 1 | AHU145 | Energy | Sensor | AHU | 1 | AHU VSD is not modulating | 2023-12-10 09:39 | 12d 23h 20m | 2023-12-10 09:39 | 0 | Closed | Online | 0
286 | The Centrepoint | Level 1 | Sensor 111 | Energy | Sensor | AHU | 2 | Air Damper is not modulating | 2023-12-11 09:39 | 7d 14h 25m | 2023-12-11 09:39 | 0 | Closed | Online | 0
287 | The Centrepoint | Level 3 | Sensor 112 | Energy | Sensor | CH | 5 | AHU is operating outside operation | 2023-12-12 09:39 | 6d 0h 35m | 2023-12-12 09:39 | 0 | Closed | Online | 0
288 | The Centrepoint | Level 3 | Sensor 113 | Energy | Sensor | CH | 6 | AHU high VSD Speed (Default >40Hz User defined) | 2023-12-13 09:39 | 37d 9h 25m | 2023-12-13 09:39 | 62.1 | Closed | Online | 4.5954
289 | The Centrepoint | Level 1 | Sensor 41 | Energy | Sensor | CH | 8 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-12-14 09:39 | 16d 8h 55m | 2023-12-14 09:39 | 0 | Closed | Online | 0
290 | The Centrepoint | Level 4 | AHU146 | Energy | Sensor | CHWP | 20 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-12-15 09:39 | 1d 22h 50m | 2023-12-15 09:39 | 0 | Closed | Online | 0
291 | The Centrepoint | Level 4 | AHU147 | Operation | Sensor | CHWP | 15 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-12-16 09:39 | 5d 3h 50m | 2023-12-16 09:39 | 0 | Closed | Online | 0
292 | The Centrepoint | Level 3 | AHU148 | Comfort | Service | CHWP | 5 | CHW CV not modulating (Out of Range/Stucked) | 2023-12-17 09:39 | 1d 2h 50m | 2023-12-17 09:39 | 21.5 | Closed | Online | 1.591
293 | The Centrepoint | Level 4 | AHU149 | Comfort | Service | CHWP | 4 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-12-18 09:39 | 7d 22h 50m | 2023-12-18 09:39 | 2 | Closed | Online | 0.148
294 | The Centrepoint | Level 3 | Sensor 114 | Comfort | Service | CHPL | 5 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-12-19 09:39 | 6d 28h 2m | 2023-12-19 09:39 | 0 | Closed | Offline | 0
295 | The Centrepoint | Level B2 | Sensor 115 | Comfort | Service | CHPL | 16 | Fault Static Pressure Sensor | 2023-12-20 09:39 | 3d 18h 30m | 2023-12-20 09:39 | 0 | Closed | Online | 0
296 | The Centrepoint | Level 4 | Sensor 116 | Comfort | Service | CT | 20 | AHU VSD is not modulating | 2023-12-21 09:39 | 13d 16h 45m | 2023-12-21 09:39 | 0 | Closed | Online | 0
297 | The Centrepoint | Level 4 | Sensor 42 | Comfort | Control | CT | 2 | Air Damper is not modulating | 2023-12-22 09:39 | 2h 10m | 2023-12-22 09:39 | 0 | Closed | Online | 0
298 | The Centrepoint | Level 4 | AHU150 | Comfort | Control | CT | 3 | AHU is operating outside operation | 2023-12-23 09:39 | 7d 14h 25m | 2023-12-23 09:39 | 0 | Closed | Online | 0
299 | The Centrepoint | Level 1 | AHU151 | Comfort | Control | CT | 1 | AHU high VSD Speed (Default >40Hz User defined) | 2023-12-24 09:39 | 12d 23h 20m | 2023-12-24 09:39 | 21.6 | Closed | Online | 1.5984
300 | The Centrepoint | Level 4 | AHU152 | Comfort | Control | CT | 25 | AHU chiller water valve faulty open (Default>100% User defined) | 2023-12-25 09:39 | 7d 14h 25m | 2023-12-25 09:39 | 3 | Open | Online | 0.222
301 | The Centrepoint | Level 1 | AHU153 | Comfort | Control | CT | 7 | Fault SA Temp Sensor (Out of Range/Flat) | 2023-12-26 09:39 | 6d 0h 35m | 2023-12-26 09:39 | 0 | In-Progress | Online | 0
302 | The Centrepoint | Level 1 | Sensor 117 | Comfort | Control | CT | 8 | Fault OC Temp Sensor (Out of Range/Flat) | 2023-12-27 09:39 | 37d 9h 25m | 2023-12-27 09:39 | 0 | In-Progress | Online | 0
303 | The Centrepoint | Level 4 | Sensor 118 | Comfort | Control | CWP | 30 | CHW CV not modulating (Out of Range/Stucked) | 2023-12-28 09:39 | 16d 8h 55m | 2023-12-28 09:39 | 0 | In-Progress | Online | 0
304 | The Centrepoint | Level 1 | Sensor 119 | Comfort | Control | CHWP | 1 | AHU SA Temp is lower than Setpoint (Overcool) | 2023-12-29 09:39 | 1d 22h 50m | 2023-12-29 09:39 | 0 | In-Progress | Online | 0
305 | The Centrepoint | Level 4 | Sensor 43 | Comfort | Control | CHWP | 2 | AHU RA Temp is lower than Setpoint (Overcool) | 2023-12-30 09:39 | 5d 3h 50m | 2023-12-30 09:39 | 35.5 | Closed | Online | 2.627
306 | The Centrepoint | Level 4 | AHU154 | Comfort | Control | CHPL | 40 | Fault Static Pressure Sensor | 2023-12-31 09:39 | 1d 2h 50m | 2023-12-31 09:39 | 620 | Open | Online | 45.88
307 | The Centrepoint | Level 3 | AHU155 | Comfort | Control | CHPL | 3 | AHU VSD is not modulating | 2024-01-01 09:39 | 7d 22h 50m | 2024-01-01 09:39 | 28 | Open | Offline | 2.072
308 | The Centrepoint | Level 4 | AHU156 | Comfort | Control | CT | 8 | Air Damper is not modulating | 2024-01-02 09:39 | 6d 28h 2m | 2024-01-02 09:39 | 20 | Open |  | 1.48
309 | The Centrepoint | Level 4 | AHU157 | Comfort | Control | CT | 1 | AHU is operating outside operation | 2024-01-03 09:39 | 3d 18h 30m | 2024-01-03 09:39 | 5 | In-Progress |  | 0.37
310 | The Centrepoint | Level 4 | Sensor 120 | Comfort | Control | CT | 3 | AHU high VSD Speed (Default >40Hz User defined) | 2024-01-04 09:39 | 13d 16h 45m | 2024-01-04 09:39 | 30 | In-Progress |  | 2.22
311 | The Centrepoint | Level 5 | Sensor 121 | Comfort | Control | CT | 5 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-01-05 09:39 | 2h 10m | 2024-01-05 09:39 | 0 | In-Progress |  | 0
312 | The Centrepoint | Level 3 | Sensor 122 | Comfort | Control | CT | 2 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-01-06 09:39 | 7d 14h 25m | 2024-01-06 09:39 | 0 | In-Progress |  | 0
313 | The Centrepoint | Level 3 | Sensor 44 | Comfort | Control | CT | 1 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-01-07 09:39 | 12d 23h 20m | 2024-01-07 09:39 | 35 | Closed |  | 2.59
314 | The Centrepoint | Level 4 | AHU158 | Comfort | Control | CT | 2 | CHW CV not modulating (Out of Range/Stucked) | 2024-01-08 09:39 | 7d 14h 25m | 2024-01-08 09:39 | 23 | Closed |  | 1.702
315 | The Centrepoint | Level B2 | AHU159 | Comfort | Control | CWP | 5 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-01-09 09:39 | 6d 0h 35m | 2024-01-09 09:39 | 0 | Closed |  | 0
316 | The Centrepoint | Level 3 | AHU160 | Comfort | Control | CWP | 6 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-01-10 09:39 | 37d 9h 25m | 2024-01-10 09:39 | 0 | Closed |  | 0
317 | The Centrepoint | Level 1 | AHU161 | Comfort | Control | CWP | 8 | Fault Static Pressure Sensor | 2024-01-11 09:39 | 16d 8h 55m | 2024-01-11 09:39 | 56 | Closed |  | 4.144
318 | The Centrepoint | Level 1 | Sensor 123 | Comfort | Control | AHU | 20 | AHU VSD is not modulating | 2024-01-12 09:39 | 1d 22h 50m | 2024-01-12 09:39 | 0 | Closed |  | 0
319 | The Centrepoint | Level 1 | Sensor 124 | Comfort | Control | AHU | 15 | Air Damper is not modulating | 2024-01-13 09:39 | 5d 3h 50m | 2024-01-13 09:39 | 69 | Closed |  | 5.106
320 | The Centrepoint | Level 4 | Sensor 125 | Comfort | Control | AHU | 5 | AHU is operating outside operation | 2024-01-14 09:39 | 1d 2h 50m | 2024-01-14 09:39 | 100 | Closed |  | 7.4
321 | The Centrepoint | Level 1 | Sensor 45 | Comfort | Control | AHU | 4 | AHU high VSD Speed (Default >40Hz User defined) | 2024-01-15 09:39 | 7d 22h 50m | 2024-01-15 09:39 | 35 | Closed |  | 2.59
322 | The Centrepoint | Level 4 | AHU162 | Comfort | Control | AHU | 5 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-01-16 09:39 | 6d 28h 2m | 2024-01-16 09:39 | 7 | Closed |  | 0.518
323 | The Centrepoint | Level 1 | AHU163 | Operation | Control | AHU | 16 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-01-17 09:39 | 3d 18h 30m | 2024-01-17 09:39 | 60 | Closed |  | 4.44
324 | The Centrepoint | Level 4 | AHU164 | Operation | Control | AHU | 20 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-01-18 09:39 | 13d 16h 45m | 2024-01-18 09:39 | 0 | Closed |  | 0
325 | Tiong Bahru Plaza | Level 3 | AHU165 | Operation | Control | AHU | 2 | CHW CV not modulating (Out of Range/Stucked) | 2024-01-19 09:39 | 2h 10m | 2024-01-19 09:39 | 120 | Closed |  | 8.88
326 | Tiong Bahru Plaza | Level 4 | Sensor 126 | Operation | Control | AHU | 3 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-01-20 09:39 | 7d 14h 25m | 2024-01-20 09:39 | 0 | Closed |  | 0
327 | Tiong Bahru Plaza | Level 3 | Sensor 127 | Operation | Control | AHU | 1 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-01-21 09:39 | 12d 23h 20m | 2024-01-21 09:39 | 0 | Closed |  | 0
328 | Tiong Bahru Plaza | Level 2 | Sensor 128 | Operation | Control | AHU | 25 | Fault Static Pressure Sensor | 2024-01-22 09:39 | 7d 14h 25m | 2024-01-22 09:39 | 0 | Closed |  | 0
329 | Tiong Bahru Plaza | Level 1 | Sensor 46 | Operation | Control | AHU | 7 | AHU VSD is not modulating | 2024-01-23 09:39 | 6d 0h 35m | 2024-01-23 09:39 | 0 | Closed |  | 0
330 | Tiong Bahru Plaza | Level 3 | AHU166 | Operation | Control | AHU | 1 | Air Damper is not modulating | 2024-01-24 09:39 | 37d 9h 25m | 2024-01-24 09:39 | 0 | Closed |  | 0
331 | Tiong Bahru Plaza | Level B1 | AHU167 | Operation | Control | AHU | 3 | AHU is operating outside operation | 2024-01-25 09:39 | 16d 8h 55m | 2024-01-25 09:39 | 62.1 | Closed |  | 4.5954
332 | Tiong Bahru Plaza | Level 4 | AHU168 | Operation | Control | AHU | 5 | AHU high VSD Speed (Default >40Hz User defined) | 2024-01-26 09:39 | 1d 22h 50m | 2024-01-26 09:39 | 0 | Closed |  | 0
333 | Tiong Bahru Plaza | Level 3 | AHU169 | Operation | Control | CH | 2 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-01-27 09:39 | 5d 3h 50m | 2024-01-27 09:39 | 0 | Closed |  | 0
334 | Tiong Bahru Plaza | Level 3 | Sensor 129 | Operation | Control | CH | 1 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-01-28 09:39 | 1d 2h 50m | 2024-01-28 09:39 | 0 | Closed |  | 0
335 | Tiong Bahru Plaza | Level B1 | Sensor 130 | Operation | Control | CH | 2 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-01-29 09:39 | 7d 22h 50m | 2024-01-29 09:39 | 0 | Closed |  | 0
336 | Tiong Bahru Plaza | Level 3 | Sensor 131 | Operation | Control | CHWP | 5 | CHW CV not modulating (Out of Range/Stucked) | 2024-01-30 09:39 | 6d 28h 2m | 2024-01-30 09:39 | 0 | Closed |  | 0
337 | Tiong Bahru Plaza | Level 4 | Sensor 47 | Operation | Control | CHWP | 6 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-01-31 09:39 | 3d 18h 30m | 2024-01-31 09:39 | 0 | Closed |  | 0
338 | Tiong Bahru Plaza | Level 1 | AHU170 | Operation | Control | CHWP | 8 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-02-01 09:39 | 13d 16h 45m | 2024-02-01 09:39 | 35.5 | Closed |  | 2.627
339 | Tiong Bahru Plaza | Level 3 | AHU171 | Operation | Control | CHWP | 20 | Fault Static Pressure Sensor | 2024-02-02 09:39 | 2h 10m | 2024-02-02 09:39 | 620 | Closed |  | 45.88
340 | Tiong Bahru Plaza | Level 4 | AHU172 | Operation | Control | CHPL | 15 | AHU VSD is not modulating | 2024-02-03 09:39 | 7d 14h 25m | 2024-02-03 09:39 | 28 | Closed |  | 2.072
341 | Tiong Bahru Plaza | Level 1 | AHU173 | Operation | Control | CHPL | 5 | Air Damper is not modulating | 2024-02-04 09:39 | 12d 23h 20m | 2024-02-04 09:39 | 20 | Closed |  | 1.48
342 | Tiong Bahru Plaza | Level 4 | Sensor 132 | Operation | Control | CT | 4 | AHU is operating outside operation | 2024-02-05 09:39 | 7d 14h 25m | 2024-02-05 09:39 | 5 | Closed |  | 0.37
343 | Tiong Bahru Plaza | Level 1 | Sensor 133 | Operation | Control | CT | 5 | AHU high VSD Speed (Default >40Hz User defined) | 2024-02-06 09:39 | 6d 0h 35m | 2024-02-06 09:39 | 30 | Closed |  | 2.22
344 | Tiong Bahru Plaza | Level 4 | Sensor 134 | Operation | Control | CT | 16 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-02-07 09:39 | 37d 9h 25m | 2024-02-07 09:39 | 0 | Closed |  | 0
345 | Tiong Bahru Plaza | Level 4 | Sensor 48 | Operation | Sensor | CT | 20 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-02-08 09:39 | 16d 8h 55m | 2024-02-08 09:39 | 0 | Closed |  | 0
346 | Tiong Bahru Plaza | Level 3 | AHU174 | Operation | Sensor | CT | 2 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-02-09 09:39 | 1d 22h 50m | 2024-02-09 09:39 | 35 | Closed |  | 2.59
347 | Tiong Bahru Plaza | Level 3 | AHU175 | Operation | Sensor | CT | 3 | CHW CV not modulating (Out of Range/Stucked) | 2024-02-10 09:39 | 5d 3h 50m | 2024-02-10 09:39 | 23 | Closed |  | 1.702
348 | Tiong Bahru Plaza | Level 1 | AHU176 | Operation | Sensor | CT | 1 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-02-11 09:39 | 1d 2h 50m | 2024-02-11 09:39 | 0 | Closed |  | 0
349 | Tiong Bahru Plaza | Level 4 | AHU177 | Operation | Sensor | CWP | 25 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-02-12 09:39 | 7d 22h 50m | 2024-02-12 09:39 | 0 | Open |  | 0
350 | Tiong Bahru Plaza | Level 1 | Sensor 135 | Operation | Sensor | CHWP | 7 | AHU VSD is not modulating | 2024-02-13 09:39 | 6d 28h 2m | 2024-02-13 09:39 | 56 | Open |  | 4.144
351 | Tiong Bahru Plaza | Level 4 | Sensor 136 | Operation | Sensor | CHWP | 8 | Air Damper is not modulating | 2024-02-14 09:39 | 3d 18h 30m | 2024-02-14 09:39 | 0 | In-Progress |  | 0
352 | Tiong Bahru Plaza | Level 4 | Sensor 137 | Operation | Sensor | CHPL | 30 | AHU is operating outside operation | 2024-02-15 09:39 | 13d 16h 45m | 2024-02-15 09:39 | 69 | In-Progress |  | 5.106
353 | Tiong Bahru Plaza | Level 4 | Sensor 49 | Operation | Sensor | CHPL | 1 | AHU high VSD Speed (Default >40Hz User defined) | 2024-02-16 09:39 | 2h 10m | 2024-02-16 09:39 | 100 | Closed |  | 7.4
354 | Tiong Bahru Plaza | Level 4 | AHU178 | Operation | Sensor | CT | 2 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-02-17 09:39 | 7d 14h 25m | 2024-02-17 09:39 | 35 | In-Progress |  | 2.59
355 | Tiong Bahru Plaza | Level 3 | AHU179 | Operation | Sensor | CT | 40 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-02-18 09:39 | 12d 23h 20m | 2024-02-18 09:39 | 7 | In-Progress |  | 0.518
356 | Tiong Bahru Plaza | Level 3 | AHU180 | Operation | Service | CT | 3 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-02-19 09:39 | 7d 14h 25m | 2024-02-19 09:39 | 60 | In-Progress |  | 4.44
357 | Tiong Bahru Plaza | Level B1 | AHU181 | Operation | Service | CT | 8 | CHW CV not modulating (Out of Range/Stucked) | 2024-02-20 09:39 | 6d 0h 35m | 2024-02-20 09:39 | 0 | In-Progress |  | 0
358 | Tiong Bahru Plaza | Level 4 | Sensor 138 | Operation | Service | CT | 1 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-02-21 09:39 | 37d 9h 25m | 2024-02-21 09:39 | 120 | Closed |  | 8.88
359 | Tiong Bahru Plaza | Level 5 | Sensor 139 | Operation | Service | CT | 3 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-02-22 09:39 | 16d 8h 55m | 2024-02-22 09:39 | 0 | Closed |  | 0
360 | Tiong Bahru Plaza | Level 1 | Sensor 140 | Operation | Service | CT | 5 | Fault Static Pressure Sensor | 2024-02-23 09:39 | 1d 22h 50m | 2024-02-23 09:39 | 0 | Closed |  | 0
361 | Tiong Bahru Plaza | Level 4 | Sensor 50 | Operation | Control | CWP | 2 | AHU VSD is not modulating | 2024-02-24 09:39 | 5d 3h 50m | 2024-02-24 09:39 | 0 | Closed |  | 0
362 | Tiong Bahru Plaza | Level 5 | AHU182 | Operation | Control | CWP | 1 | Air Damper is not modulating | 2024-02-25 09:39 | 1d 2h 50m | 2024-02-25 09:39 | 0 | Closed |  | 0
363 | Tiong Bahru Plaza | Level 5 | AHU183 | Operation | Control | CWP | 2 | AHU is operating outside operation | 2024-02-26 09:39 | 7d 22h 50m | 2024-02-26 09:39 | 0 | Closed |  | 0
364 | Tiong Bahru Plaza | Level 1 | AHU184 | Operation | Control | AHU | 5 | AHU high VSD Speed (Default >40Hz User defined) | 2024-02-27 09:39 | 6d 28h 2m | 2024-02-27 09:39 | 62.1 | Closed |  | 4.5954
365 | Tiong Bahru Plaza | Level 5 | AHU185 | Operation | Control | AHU | 8 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-02-28 09:39 | 3d 18h 30m | 2024-02-28 09:39 | 0 | Closed |  | 0
366 | Tiong Bahru Plaza | Level 1 | Sensor 141 | Operation | Control | AHU | 30 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-02-29 09:39 | 13d 16h 45m | 2024-02-29 09:39 | 0 | Closed |  | 0
367 | Tiong Bahru Plaza | Level B2 | Sensor 142 | Operation | Control | AHU | 1 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-03-01 09:39 | 2h 10m | 2024-03-01 09:39 | 0 | Closed |  | 0
368 | Tiong Bahru Plaza | Level 4 | Sensor 143 | Operation | Control | AHU | 2 | CHW CV not modulating (Out of Range/Stucked) | 2024-03-02 09:39 | 7d 14h 25m | 2024-03-02 09:39 | 21.5 | Closed |  | 1.591
369 | Waterway Point | Level B1 | Sensor 51 | Operation | Control | AHU | 40 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-03-03 09:39 | 12d 23h 20m | 2024-03-03 09:39 | 2 | Closed |  | 0.148
370 | Waterway Point | Level 4 | AHU186 | Operation | Control | AHU | 3 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-03-04 09:39 | 7d 14h 25m | 2024-03-04 09:39 | 0 | Closed |  | 0
371 | Waterway Point | Level 3 | AHU187 | Operation | Control | AHU | 8 | Fault Static Pressure Sensor | 2024-03-05 09:39 | 6d 0h 35m | 2024-03-05 09:39 | 0 | Closed |  | 0
372 | Waterway Point | Level 4 | AHU188 | Operation | Control | AHU | 1 | AHU VSD is not modulating | 2024-03-06 09:39 | 37d 9h 25m | 2024-03-06 09:39 | 0 | Closed |  | 0
373 | Waterway Point | Level 4 | AHU189 | Operation | Control | AHU | 3 | Air Damper is not modulating | 2024-03-07 09:39 | 16d 8h 55m | 2024-03-07 09:39 | 0 | Closed |  | 0
374 | Waterway Point | Level 4 | Sensor 144 | Operation | Control | AHU | 5 | AHU is operating outside operation | 2024-03-08 09:39 | 1d 22h 50m | 2024-03-08 09:39 | 0 | Closed |  | 0
375 | Waterway Point | Level 4 | Sensor 145 | Operation | Control | AHU | 2 | AHU high VSD Speed (Default >40Hz User defined) | 2024-03-09 09:39 | 5d 3h 50m | 2024-03-09 09:39 | 21.6 | Closed |  | 1.5984
376 | Waterway Point | Level 3 | Sensor 146 | Operation | Control | AHU | 1 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-03-10 09:39 | 1d 2h 50m | 2024-03-10 09:39 | 3 | Closed |  | 0.222
377 | Waterway Point | Level 4 | Sensor 52 | Operation | Control | AHU | 2 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-03-11 09:39 | 7d 22h 50m | 2024-03-11 09:39 | 0 | Closed |  | 0
378 | Waterway Point | Level 4 | AHU190 | Operation | Control | AHU | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-03-12 09:39 | 6d 28h 2m | 2024-03-12 09:39 | 0 | Closed |  | 0
379 | Waterway Point | Level 4 | AHU191 | Operation | Control | CH | 6 | CHW CV not modulating (Out of Range/Stucked) | 2024-03-13 09:39 | 3d 18h 30m | 2024-03-13 09:39 | 0 | Closed |  | 0
380 | Waterway Point | Level 3 | AHU192 | Operation | Control | CH | 8 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-03-14 09:39 | 13d 16h 45m | 2024-03-14 09:39 | 0 | Closed |  | 0
381 | Waterway Point | Level 1 | AHU193 | Operation | Control | CH | 20 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-03-15 09:39 | 2h 10m | 2024-03-15 09:39 | 35.5 | Closed |  | 2.627
382 | Waterway Point | Level 4 | Sensor 147 | Operation | Control | CHWP | 15 | Fault Static Pressure Sensor | 2024-03-16 09:39 | 7d 14h 25m | 2024-03-16 09:39 | 620 | Closed |  | 45.88
383 | Waterway Point | Level 3 | Sensor 148 | Operation | Control | CHWP | 5 | AHU VSD is not modulating | 2024-03-17 09:39 | 12d 23h 20m | 2024-03-17 09:39 | 28 | In-Progress |  | 2.072
384 | Waterway Point | Level 4 | Sensor 149 | Operation | Control | CHWP | 4 | Air Damper is not modulating | 2024-03-18 09:39 | 7d 14h 25m | 2024-03-18 09:39 | 20 | Open |  | 1.48
385 | Waterway Point | Level 3 | Sensor 53 | Operation | Control | CHWP | 5 | AHU is operating outside operation | 2024-03-19 09:39 | 6d 0h 35m | 2024-03-19 09:39 | 5 | In-Progress |  | 0.37
386 | Waterway Point | Level 3 | AHU194 | Operation | Control | CHPL | 16 | AHU high VSD Speed (Default >40Hz User defined) | 2024-03-20 09:39 | 37d 9h 25m | 2024-03-20 09:39 | 30 | In-Progress |  | 2.22
387 | Waterway Point | Level 5 | AHU195 | Operation | Control | CHPL | 20 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-03-21 09:39 | 16d 8h 55m | 2024-03-21 09:39 | 0 | Closed |  | 0
388 | Waterway Point | Level 4 | AHU196 | Operation | Control | CT | 2 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-03-22 09:39 | 1d 22h 50m | 2024-03-22 09:39 | 0 | Closed |  | 0
389 | Waterway Point | Level 1 | AHU197 | Operation | Control | CT | 3 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-03-23 09:39 | 5d 3h 50m | 2024-03-23 09:39 | 35 | Closed |  | 2.59
390 | Waterway Point | Level 3 | Sensor 150 | Operation | Control | CT | 1 | CHW CV not modulating (Out of Range/Stucked) | 2024-03-24 09:39 | 1d 2h 50m | 2024-03-24 09:39 | 23 | Closed |  | 1.702
391 | White Sands | Level 3 | Sensor 151 | Operation | Control | CT | 25 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-03-25 09:39 | 7d 22h 50m | 2024-03-25 09:39 | 0 | Closed |  | 0
392 | White Sands | Level 2 | Sensor 152 | Operation | Control | CT | 7 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-03-26 09:39 | 6d 28h 2m | 2024-03-26 09:39 | 0 | Closed |  | 0
393 | White Sands | Level 2 | Sensor 54 | Operation | Control | CT | 8 | Fault Static Pressure Sensor | 2024-03-27 09:39 | 3d 18h 30m | 2024-03-27 09:39 | 56 | Closed |  | 4.144
394 | White Sands | Level 1 | AHU198 | Operation | Control | CT | 30 | AHU VSD is not modulating | 2024-03-28 09:39 | 13d 16h 45m | 2024-03-28 09:39 | 0 | Closed |  | 0
395 | White Sands | Level 3 | AHU199 | Operation | Control | CWP | 1 | Air Damper is not modulating | 2024-03-29 09:39 | 2h 10m | 2024-03-29 09:39 | 69 | Closed |  | 5.106
396 | White Sands | Level 3 | AHU200 | Operation | Control | CWP | 2 | AHU is operating outside operation | 2024-03-30 09:39 | 7d 14h 25m | 2024-03-30 09:39 | 100 | Closed |  | 7.4
397 | White Sands | Level 4 | AHU201 | Operation | Control | CWP | 40 | AHU high VSD Speed (Default >40Hz User defined) | 2024-03-31 09:39 | 12d 23h 20m | 2024-03-31 09:39 | 35 | Closed |  | 2.59
398 | White Sands | Level 3 | Sensor 153 | Operation | Control | CWP | 3 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-04-01 09:39 | 7d 14h 25m | 2024-04-01 09:39 | 7 | Closed |  | 0.518
399 | White Sands | Level 4 | Sensor 154 | Operation | Control | AHU | 8 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-04-02 09:39 | 6d 0h 35m | 2024-04-02 09:39 | 60 | Closed |  | 4.44
400 | White Sands | Level 3 | Sensor 155 | Operation | Control | AHU | 1 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-04-03 09:39 | 37d 9h 25m | 2024-04-03 09:39 | 0 | Closed |  | 0
401 | White Sands | Level 3 | Sensor 55 | Operation | Control | AHU | 3 | CHW CV not modulating (Out of Range/Stucked) | 2024-04-04 09:39 | 16d 8h 55m | 2024-04-04 09:39 | 120 | Closed |  | 8.88
402 | White Sands | Level B1 | AHU202 | Operation | Control | CT | 5 | AHU SA Temp is lower than Setpoint (Overcool) | 2024-04-05 09:39 | 1d 22h 50m | 2024-04-05 09:39 | 0 | In-Progress |  | 0
403 | White Sands | Level 4 | AHU203 | Operation | Control | CT | 2 | AHU RA Temp is lower than Setpoint (Overcool) | 2024-04-06 09:39 | 5d 3h 50m | 2024-04-06 09:39 | 0 | In-Progress |  | 0
404 | White Sands | Level 3 | AHU204 | Operation | Control | CWP | 1 | Fault Static Pressure Sensor | 2024-04-07 09:39 | 1d 2h 50m | 2024-04-07 09:39 | 0 | Open |  | 0
405 | White Sands | Level 1 | AHU205 | Operation | Control | CWP | 2 | AHU VSD is not modulating | 2024-04-08 09:39 | 7d 22h 50m | 2024-04-08 09:39 | 0 | Closed |  | 0
406 | White Sands | Level B1 | Sensor 156 | Operation | Control | CT | 5 | Air Damper is not modulating | 2024-04-09 09:39 | 6d 28h 2m | 2024-04-09 09:39 | 0 | In-Progress |  | 0
407 | White Sands | Level 3 | Sensor 157 | Operation | Control | CT | 6 | AHU is operating outside operation | 2024-04-10 09:39 | 3d 18h 30m | 2024-04-10 09:39 | 62.1 | Closed |  | 4.5954
408 | White Sands | Level 3 | Sensor 158 | Operation | Control | CWP | 8 | AHU high VSD Speed (Default >40Hz User defined) | 2024-04-11 09:39 | 13d 16h 45m | 2024-04-11 09:39 | 0 | Closed |  | 0
409 | White Sands | Level 1 | Sensor 56 | Operation | Sensor | CWP | 20 | AHU chiller water valve faulty open (Default>100% User defined) | 2024-04-12 09:39 | 2h 10m | 2024-04-12 09:39 | 0 | Closed |  | 0
410 | White Sands | Level 1 | AHU206 | Operation | Sensor | CWP | 15 | Fault SA Temp Sensor (Out of Range/Flat) | 2024-04-13 09:39 | 7d 14h 25m | 2024-04-13 09:39 | 0 | Closed |  | 0
411 | White Sands | Level 5 | AHU207 | Operation | Sensor | CWP | 5 | Fault OC Temp Sensor (Out of Range/Flat) | 2024-04-14 09:39 | 12d 23h 20m | 2024-04-14 09:39 | 21.5 | Closed |  | 1.591
412 | White Sands | Level 4 | AHU208 | Operation | Sensor | AHU | 4 | CHW CV not modulating (Out of Range/Stucked) | 2024-04-15 09:39 | 7d 14h 25m | 2024-04-15 09:39 | 2 | Closed |  | 0.148

## Chiller
Name | Mall Name | Datetime | Building Load | CH Plant kW | CH Plant Total kW | CHW Flow | Efficiency | HEAT BALANCE | Heat Rejection
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.15264 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 1:00:00 am | 0.15264 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 2:00:00 am | 0.15264 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 am | 0.15264 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 4:00:00 am | 0.15264 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | North Point City (North Wing) | 29/7/2024 5:00:00 am | 0.15264 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | North Point City (North Wing) | 29/7/2024 6:00:00 am | 230.1518 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | North Point City (North Wing) | 29/7/2024 7:00:00 am | 353.595 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | North Point City (North Wing) | 29/7/2024 8:00:00 am | 232.9173 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | North Point City (North Wing) | 29/7/2024 9:00:00 am | 258.2021 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | North Point City (North Wing) | 29/7/2024 10:00:00 am | 258.2727 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | North Point City (North Wing) | 29/7/2024 11:00:00 am | 259.1299 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | North Point City (North Wing) | 29/7/2024 12:00:00 pm | 258.5767 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | North Point City (North Wing) | 29/7/2024 1:00:00 pm | 374.6179 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | North Point City (North Wing) | 29/7/2024 2:00:00 pm | 356.8681 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 353.213 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | North Point City (North Wing) | 29/7/2024 4:00:00 pm | 367.8326 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | North Point City (North Wing) | 29/7/2024 5:00:00 pm | 364.8911 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | North Point City (North Wing) | 29/7/2024 6:00:00 pm | 322.467 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | North Point City (North Wing) | 29/7/2024 6:00:00 pm | 219.8944 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | North Point City (North Wing) | 29/7/2024 7:00:00 pm | 156.8479 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | North Point City (North Wing) | 29/7/2024 8:00:00 pm | 209.2716 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | North Point City (North Wing) | 29/7/2024 9:00:00 pm | 10.5742 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | North Point City (North Wing) | 29/7/2024 10:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | North Point City (North Wing) | 29/7/2024 11:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | North Point City (North Wing) | 30/7/2024 12:00:00 am | 0 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 30/7/2024 1:00:00 am | 0.007655 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | North Point City (North Wing) | 30/7/2024 2:00:00 am | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 30/7/2024 3:00:00 am | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 30/7/2024 4:00:00 am | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 30/7/2024 5:00:00 am | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | North Point City (North Wing) | 30/7/2024 6:00:00 am | 8.3935 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | North Point City (North Wing) | 30/7/2024 7:00:00 am | 383.8692 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | North Point City (North Wing) | 30/7/2024 8:00:00 am | 229.3992 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | North Point City (North Wing) | 30/7/2024 9:00:00 am | 253.1832 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | North Point City (North Wing) | 30/7/2024 10:00:00 am | 253.8745 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | North Point City (North Wing) | 30/7/2024 11:00:00 am | 309.7934 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | North Point City (North Wing) | 30/7/2024 12:00:00 pm | 353.5703 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | North Point City (North Wing) | 30/7/2024 1:00:00 pm | 247.2451 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | North Point City (North Wing) | 30/7/2024 2:00:00 pm | 250.1999 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | North Point City (North Wing) | 30/7/2024 3:00:00 pm | 249.9489 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | North Point City (North Wing) | 30/7/2024 4:00:00 pm | 252.2253 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | North Point City (North Wing) | 30/7/2024 5:00:00 pm | 259.2637 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | North Point City (North Wing) | 30/7/2024 6:00:00 pm | 255.7154 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | North Point City (North Wing) | 30/7/2024 6:00:00 pm | 237.3407 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | North Point City (North Wing) | 30/7/2024 7:00:00 pm | 230.4723 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | North Point City (North Wing) | 30/7/2024 8:00:00 pm | 214.3843 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | North Point City (North Wing) | 30/7/2024 9:00:00 pm | 8.1023 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | North Point City (North Wing) | 30/7/2024 10:00:00 pm | 0 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | North Point City (North Wing) | 30/7/2024 11:00:00 pm | 0 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | North Point City (North Wing) | 31/7/2024 12:00:00 am | 0 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 31/7/2024 1:00:00 am | 0 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 31/7/2024 2:00:00 am | 0 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 31/7/2024 3:00:00 am | 0 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 31/7/2024 4:00:00 am | 0 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 31/7/2024 5:00:00 am | 0 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 31/7/2024 6:00:00 am | 7.2616 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | North Point City (North Wing) | 31/7/2024 7:00:00 am | 382.2976 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | North Point City (North Wing) | 31/7/2024 8:00:00 am | 214.4432 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | North Point City (North Wing) | 31/7/2024 9:00:00 am | 230.3184 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | North Point City (North Wing) | 31/7/2024 10:00:00 am | 250.4467 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | North Point City (North Wing) | 31/7/2024 11:00:00 am | 253.9743 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | North Point City (North Wing) | 31/7/2024 12:00:00 pm | 251.2279 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | North Point City (North Wing) | 31/7/2024 1:00:00 pm | 250.5016 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | North Point City (North Wing) | 31/7/2024 2:00:00 pm | 252.5164 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | North Point City (North Wing) | 31/7/2024 3:00:00 pm | 255.5416 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | North Point City (North Wing) | 31/7/2024 4:00:00 pm | 257.9506 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | North Point City (North Wing) | 31/7/2024 5:00:00 pm | 257.7903 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | North Point City (North Wing) | 31/7/2024 6:00:00 pm | 247.8403 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | North Point City (North Wing) | 31/7/2024 6:00:00 pm | 240.8013 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | North Point City (North Wing) | 31/7/2024 7:00:00 pm | 219.9641 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | North Point City (North Wing) | 31/7/2024 8:00:00 pm | 200.6285 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | North Point City (North Wing) | 31/7/2024 9:00:00 pm | 10.0851 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | North Point City (North Wing) | 31/7/2024 10:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 31/7/2024 11:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 1/8/2024 12:00:00 am | 0 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | North Point City (North Wing) | 1/8/2024 1:00:00 am | 0 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | North Point City (North Wing) | 1/8/2024 2:00:00 am | 0 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | North Point City (North Wing) | 1/8/2024 3:00:00 am | 0 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | North Point City (North Wing) | 1/8/2024 4:00:00 am | 0 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | North Point City (North Wing) | 1/8/2024 5:00:00 am | 0 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | North Point City (North Wing) | 1/8/2024 6:00:00 am | 7.4451 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | North Point City (North Wing) | 1/8/2024 7:00:00 am | 341.0601 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | North Point City (North Wing) | 1/8/2024 8:00:00 am | 208.3729 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | North Point City (North Wing) | 1/8/2024 9:00:00 am | 216.7669 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | North Point City (North Wing) | 1/8/2024 10:00:00 am | 252.1507 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | North Point City (North Wing) | 1/8/2024 11:00:00 am | 251.3926 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | North Point City (North Wing) | 1/8/2024 12:00:00 pm | 248.3258 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | North Point City (North Wing) | 1/8/2024 1:00:00 pm | 250.021 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | North Point City (North Wing) | 1/8/2024 2:00:00 pm | 252.2408 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | North Point City (North Wing) | 1/8/2024 3:00:00 pm | 246.6578 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | North Point City (North Wing) | 1/8/2024 4:00:00 pm | 256.239 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | North Point City (North Wing) | 1/8/2024 5:00:00 pm | 259.0186 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | North Point City (North Wing) | 1/8/2024 6:00:00 pm | 240.1991 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | North Point City (North Wing) | 1/8/2024 6:00:00 pm | 246.6867 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | North Point City (North Wing) | 1/8/2024 7:00:00 pm | 222.663 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | North Point City (North Wing) | 1/8/2024 8:00:00 pm | 200.1667 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | North Point City (North Wing) | 1/8/2024 9:00:00 pm | 10.4129 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | North Point City (North Wing) | 1/8/2024 10:00:00 pm | 0 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | North Point City (North Wing) | 1/8/2024 11:00:00 pm | 0 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | North Point City (North Wing) | 2/8/2024 12:00:00 am | 0 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | North Point City (North Wing) | 2/8/2024 1:00:00 am | 0 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | North Point City (North Wing) | 2/8/2024 2:00:00 am | 0 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | North Point City (North Wing) | 2/8/2024 3:00:00 am | 0 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | North Point City (North Wing) | 2/8/2024 4:00:00 am | 0 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | North Point City (North Wing) | 2/8/2024 5:00:00 am | 0 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | North Point City (North Wing) | 2/8/2024 6:00:00 am | 0.9848 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | North Point City (North Wing) | 2/8/2024 7:00:00 am | 346.465 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | North Point City (North Wing) | 2/8/2024 8:00:00 am | 209.1722 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | North Point City (North Wing) | 2/8/2024 9:00:00 am | 214.7381 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | North Point City (North Wing) | 2/8/2024 10:00:00 am | 216.052 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | North Point City (North Wing) | 2/8/2024 11:00:00 am | 214.4598 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | North Point City (North Wing) | 2/8/2024 12:00:00 pm | 252.7742 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | North Point City (North Wing) | 2/8/2024 1:00:00 pm | 248.0521 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | North Point City (North Wing) | 2/8/2024 2:00:00 pm | 249.4566 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | North Point City (North Wing) | 2/8/2024 3:00:00 pm | 246.539 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766
CH_PLANT | North Point City (North Wing) | 2/8/2024 4:00:00 pm | 255.1459 | 131.7272 | 159.2118 | 41.079 | 0.62344 | -0.10051 | 0.040715
CH_PLANT | North Point City (North Wing) | 2/8/2024 5:00:00 pm | 252.438 | 139.838 | 159.4572 | 40.9576 | 0.63158 | -0.10622 | 0.037693
CH_PLANT | North Point City (North Wing) | 2/8/2024 6:00:00 pm | 235.5223 | 142.3787 | 156.58 | 40.127 | 0.65917 | -0.059145 | 0.037693
CH_PLANT | North Point City (North Wing) | 2/8/2024 6:00:00 pm | 240.9999 | 142.9808 | 159.9854 | 40.9299 | 0.67922 | -0.084936 | 0.037693
CH_PLANT | North Point City (North Wing) | 2/8/2024 7:00:00 pm | 217.6346 | 141.9497 | 150.8555 | 40.908 | 0.69374 | -0.10325 | 0.035985
CH_PLANT | North Point City (North Wing) | 2/8/2024 8:00:00 pm | 197.8981 | 142.9197 | 138.1777 | 40.916 | 0.69775 | -0.10198 | 0.027444
CH_PLANT | North Point City (North Wing) | 2/8/2024 9:00:00 pm | 7.8362 | 141.6483 | 6.752 | 3.4926 | 83.086 | -0.10838 | 0.027444
CH_PLANT | North Point City (North Wing) | 2/8/2024 10:00:00 pm | 0 | 137.604 | 0.84 | 0.027 | 100 | -0.11046 | 0.027444
CH_PLANT | North Point City (North Wing) | 2/8/2024 11:00:00 pm | 0 | 140.7528 | 0.84 | 0.027 | 100 | -0.10784 | 5.3268
CH_PLANT | North Point City (North Wing) | 3/8/2024 12:00:00 am | 0 | 136.84 | 0.84 | 0.027 | 100 | -0.11336 | 1989.365
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1556 | 141.4985 | 1.23 | 0.024 | 6.6646 | -0.11491 | 1021.944
CH_PLANT | Tampines 1 | 29/7/2024 1:00:00 am | 0.1556 | 0.83 | 1.23 | 0.024 | 7.3577 | -0.10588 | 0.549
CH_PLANT | Tampines 1 | 29/7/2024 2:00:00 am | 0.1556 | 0.83 | 1.23 | 0.024 | 5.7515 | -0.11082 | 0.032093
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 am | 0.1556 | 0.83 | 1.23 | 0.024 | 7.6403 | -0.13482 | 0.033581
CH_PLANT | Tampines 1 | 29/7/2024 4:00:00 am | 0.1556 | 0.83 | 1.23 | 0.024 | 6.4198 | -0.08407 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 5:00:00 am | 0.1556 | 0.83 | 1.23 | 0.024 | 5.6763 | -0.11678 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 6:00:00 am | 228.7117 | 0.83 | 145.6395 | 36.886 | 4.3894 | -0.11124 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 7:00:00 am | 355.3201 | 0.83 | 263.8778 | 70.8171 | 0.74909 | -0.11493 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 8:00:00 am | 213.9598 | 0.83 | 143.6267 | 42.9785 | 0.68202 | -0.09018 | 0.020435
CH_PLANT | Tampines 1 | 29/7/2024 9:00:00 am | 227.4719 | 0.83 | 150.3923 | 40.7452 | 0.66066 | -0.10321 | 0.018327
CH_PLANT | Tampines 1 | 29/7/2024 10:00:00 am | 256.7935 | 0.83 | 157.531 | 40.9629 | 0.61277 | -0.11586 | 0.018327
CH_PLANT | Tampines 1 | 29/7/2024 11:00:00 am | 258.2658 | 0.83 | 159.9617 | 40.9678 | 0.61821 | -0.10567 | 0.018327
CH_PLANT | Tampines 1 | 29/7/2024 12:00:00 pm | 257.7781 | 0.83 | 160.407 | 41.0693 | 0.6237 | -0.093901 | 2.9502
CH_PLANT | Tampines 1 | 29/7/2024 1:00:00 pm | 255.4046 | 280.394 | 159.2295 | 41.0961 | 0.62318 | -0.14155 | 1566.063
CH_PLANT | Tampines 1 | 29/7/2024 2:00:00 pm | 251.9179 | 170.7897 | 160.1795 | 41.1538 | 0.63567 | -0.20497 | 1005.043
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 253.6264 | 142.1868 | 158.8533 | 41.0918 | 0.62736 | -0.077332 | 0.57226
CH_PLANT | Tampines 1 | 29/7/2024 4:00:00 pm | 255.6177 | 140.9953 | 154.8203 | 41.0734 | 0.60607 | -0.093229 | 0.061741
CH_PLANT | Tampines 1 | 29/7/2024 5:00:00 pm | 259.834 | 141.3117 | 158.0203 | 41.1464 | 0.60867 | -0.10299 | 0.074108
CH_PLANT | Tampines 1 | 29/7/2024 6:00:00 pm | 240.9619 | 142.0145 | 153.75 | 40.447 | 0.62025 | -0.10932 | 0.06796
CH_PLANT | Tampines 1 | 29/7/2024 6:00:00 pm | 251.8262 | 142.7058 | 158.8163 | 40.9356 | 0.65941 | -0.093705 | 0.061262
CH_PLANT | Tampines 1 | 29/7/2024 7:00:00 pm | 0 | 139.9993 | 1.7892 | 1.4081 | 15.9491 | -0.092 | 0.056499
CH_PLANT | Tampines 1 | 29/7/2024 8:00:00 pm | 0 | 139.8698 | 1.46 | 0.024 | 15.9491 | -0.10716 | 0.048864
CH_PLANT | Tampines 1 | 29/7/2024 9:00:00 pm | 0 | 140.4943 | 314.0868 | 0.024 | 33.2896 | -0.10601 | 0.046605
CH_PLANT | Tampines 1 | 29/7/2024 10:00:00 pm | 0.018348 | 138.0458 | 192.8402 | 0.024 | 25.2073 | -0.097927 | 0.038783
CH_PLANT | Tampines 1 | 29/7/2024 11:00:00 pm | 0.050039 | 135.91 | 159.6322 | 0.024 | 16.7405 | -0.10611 | 0.029609
CH_PLANT | Tampines 1 | 30/7/2024 12:00:00 am | 0.08488 | 142.3993 | 158.3218 | 0.024 | 9.9003 | -0.13031 | 0.027377
CH_PLANT | Tampines 1 | 30/7/2024 1:00:00 am | 0.10103 | 221.4172 | 158.681 | 0.024 | 12.0921 | -0.076295 | 7.2576
CH_PLANT | Tampines 1 | 30/7/2024 2:00:00 am | 0.10103 | 137.7345 | 159.248 | 0.024 | 8.3197 | -0.10132 | 1667.161
CH_PLANT | Tampines 1 | 30/7/2024 3:00:00 am | 0.10103 | 144.3753 | 159.9183 | 0.024 | 7.8482 | -0.11949 | 961.0121
CH_PLANT | Tampines 1 | 30/7/2024 4:00:00 am | 0.12238 | 143.3145 | 157.141 | 0.024 | 8.5625 | -0.11649 | 0.26549
CH_PLANT | Tampines 1 | 30/7/2024 5:00:00 am | 0.12342 | 142.7942 | 157.0072 | 0.024 | 6.1329 | -0.11532 | 0.048098
CH_PLANT | Tampines 1 | 30/7/2024 6:00:00 am | 2.1066 | 142.8697 | 157.6587 | 1.2388 | 7.6569 | -0.11547 | 0.052442
CH_PLANT | Tampines 1 | 30/7/2024 7:00:00 am | 466.5208 | 143.6523 | 155.0962 | 72.8287 | 0.67636 | -0.12133 | 0.052442
CH_PLANT | Tampines 1 | 30/7/2024 8:00:00 am | 281.7451 | 144.2565 | 153.18 | 50.2432 | 0.67834 | -0.11666 | 0.046237
CH_PLANT | Tampines 1 | 30/7/2024 9:00:00 am | 250.7421 | 143.0503 | 159.5095 | 41.0497 | 0.63689 | -0.11995 | 0.041877
CH_PLANT | Tampines 1 | 30/7/2024 10:00:00 am | 252.4842 | 141.0682 | 1.8083 | 41.0843 | 0.62837 | -0.10615 | 0.037509
CH_PLANT | Tampines 1 | 30/7/2024 11:00:00 am | 252.6122 | 144.078 | 0.84 | 41.1265 | 0.62826 | -0.11515 | 0.037509
CH_PLANT | Tampines 1 | 30/7/2024 12:00:00 pm | 253.672 | 145.99 | 0.84 | 40.9531 | 0.6288 | -0.13933 | 0.033416
CH_PLANT | Tampines 1 | 30/7/2024 1:00:00 pm | 250.5889 | 140.0364 | 0.84 | 41.0044 | 0.6375 | -0.096132 | 0.026347
CH_PLANT | Tampines 1 | 30/7/2024 2:00:00 pm | 250.9931 | 1.2 | 0.84 | 41.0585 | 0.6279 | -0.11237 | 0.026347
CH_PLANT | Tampines 1 | 30/7/2024 3:00:00 pm | 252.1361 | 1.2 | 0.84 | 41.0366 | 0.62291 | -0.11498 | 3.4504
CH_PLANT | Tampines 1 | 30/7/2024 4:00:00 pm | 256.1362 | 1.2 | 0.84 | 40.9098 | 0.61563 | -0.12037 | 1666.068
CH_PLANT | Tampines 1 | 30/7/2024 5:00:00 pm | 255.5206 | 1.2 | 0.84 | 41.0441 | 0.60789 | -0.12485 | 1008.752
CH_PLANT | Tampines 1 | 30/7/2024 6:00:00 pm | 237.5489 | 1.2 | 0.84 | 42.061 | 0.58872 | -0.12308 | 0.41415
CH_PLANT | Tampines 1 | 30/7/2024 6:00:00 pm | 257.2703 | 1.2 | 0.84 | 40.914 | 0.68759 | -0.11821 | 0.049389
CH_PLANT | Tampines 1 | 30/7/2024 7:00:00 pm | 0 | 1.2 | 0.84 | 1.4067 | 21.9641 | -0.11876 | 0.049699
CH_PLANT | Tampines 1 | 30/7/2024 8:00:00 pm | 0 | 1.2 | 1.2152 | 0.027117 | 21.9641 | -0.1167 | 0.044414
CH_PLANT | Tampines 1 | 30/7/2024 9:00:00 pm | 0 | 1.2 | 250.7245 | 0.029483 | 34.4065 | -0.16476 | 0.042329
CH_PLANT | Tampines 1 | 30/7/2024 10:00:00 pm | 0.006012 | 1.2 | 157.5758 | 0.02985 | 26.4288 | -0.086652 | 0.033989
CH_PLANT | Tampines 1 | 30/7/2024 11:00:00 pm | 0.051535 | 1.2 | 161.7642 | 0.03025 | 20.06 | -0.10189 | 0.001006
CH_PLANT | Tampines 1 | 31/7/2024 12:00:00 am | 0.054998 | 1.2 | 160.5303 | 0.03 | 10.5145 | -0.12355 | 0.001006
CH_PLANT | Tampines 1 | 31/7/2024 1:00:00 am | 0.10348 | 240.5975 | 159.9868 | 0.029833 | 10.3076 | -0.12614 | 0.001006
CH_PLANT | Tampines 1 | 31/7/2024 2:00:00 am | 0.10348 | 124.592 | 159.9677 | 0.029833 | 9.8666 | -0.12018 | 0.001006
CH_PLANT | Tampines 1 | 31/7/2024 3:00:00 am | 0.10348 | 136.7727 | 160.8637 | 0.028783 | 7.3602 | -0.11768 | 0.001006
CH_PLANT | Tampines 1 | 31/7/2024 4:00:00 am | 0.10603 | 131.7778 | 161.479 | 0.030667 | 9.7727 | -0.11644 | 0.001006
CH_PLANT | Tampines 1 | 31/7/2024 5:00:00 am | 0.14557 | 136.76 | 160.0555 | 0.030167 | 6.3896 | -0.11919 | 1009.799
CH_PLANT | Tampines 1 | 31/7/2024 6:00:00 am | 1.0335 | 140.0172 | 158.195 | 0.69977 | 7.0595 | -0.11297 | 1671.116
CH_PLANT | Tampines 1 | 31/7/2024 7:00:00 am | 365.0632 | 143.072 | 161.273 | 61.9782 | 0.66109 | -0.11959 | 1036.345
CH_PLANT | Tampines 1 | 31/7/2024 8:00:00 am | 241.2598 | 142.5625 | 162.53 | 45.4487 | 0.65936 | -0.10959 | 0.24878
CH_PLANT | Tampines 1 | 31/7/2024 9:00:00 am | 256.4374 | 142.6107 | 157.0676 | 41.1473 | 0.63108 | -0.10163 | 0.045289
CH_PLANT | Tampines 1 | 31/7/2024 10:00:00 am | 250.4759 | 145.348 | 2.1613 | 41.0763 | 0.64021 | -0.1187 | 0.044205
CH_PLANT | Tampines 1 | 31/7/2024 11:00:00 am | 250.2886 | 265.565 | 1.23 | 41.0747 | 0.63828 | -0.097798 | 0.044205
CH_PLANT | Tampines 1 | 31/7/2024 12:00:00 pm | 249.0823 | 239.71 | 1.23 | 41.1149 | 0.64312 | -0.12404 | 0.037228
CH_PLANT | Tampines 1 | 31/7/2024 1:00:00 pm | 250.0226 | 143.6597 | 1.23 | 41.0748 | 0.64221 | -0.12684 | 0.032892
CH_PLANT | Tampines 1 | 31/7/2024 2:00:00 pm | 248.6463 | 244.3348 | 1.23 | 41.0344 | 0.64824 | -0.11608 | 0.032892
CH_PLANT | Tampines 1 | 31/7/2024 3:00:00 pm | 247.9583 | 128.6923 | 1.23 | 41.0037 | 0.6462 | -0.11577 | 0.032892
CH_PLANT | Tampines 1 | 31/7/2024 4:00:00 pm | 254.4522 | 141.4727 | 1.23 | 41.1388 | 0.621 | -0.11551 | 0.032892
CH_PLANT | Tampines 1 | 31/7/2024 5:00:00 pm | 257.9779 | 142.4573 | 1.23 | 41.1382 | 0.62535 | -0.10978 | 0.032892
CH_PLANT | Tampines 1 | 31/7/2024 6:00:00 pm | 230.4184 | 140.9642 | 1.23 | 40.495 | 0.63516 | -0.14848 | 0.032892
CH_PLANT | Tampines 1 | 31/7/2024 6:00:00 pm | 249.0892 | 143.3018 | 1.23 | 40.8738 | 0.73453 | -0.21519 | 5.9819
CH_PLANT | Tampines 1 | 31/7/2024 7:00:00 pm | 0 | 141.8913 | 1.23 | 1.2019 | 38.2672 | -0.13602 | 2016.554
CH_PLANT | Tampines 1 | 31/7/2024 8:00:00 pm | 0 | 142.2788 | 1.9288 | 0.022833 | 38.2672 | -0.10063 | 1028.995
CH_PLANT | Tampines 1 | 31/7/2024 9:00:00 pm | 0 | 140.1968 | 276.5095 | 0.025517 | 38.2672 | -0.11335 | 0.46443
CH_PLANT | Tampines 1 | 31/7/2024 10:00:00 pm | 0 | 141.3907 | 145.4742 | 0.02915 | 47.7725 | -0.11737 | 0.087425
CH_PLANT | Tampines 1 | 31/7/2024 11:00:00 pm | 0.035571 | 140.492 | 156.0923 | 0.029017 | 25.0666 | -0.12104 | 0.093489
CH_PLANT | Tampines 1 | 1/8/2024 12:00:00 am | 0.052055 | 139.35 | 151.097 | 0.028836 | 12.7812 | -0.1182 | 0.082881
CH_PLANT | Tampines 1 | 1/8/2024 1:00:00 am | 0.064883 | 141.1839 | 155.9507 | 0.024383 | 11.9719 | -0.11327 | 0.071217
CH_PLANT | Tampines 1 | 1/8/2024 2:00:00 am | 0.10337 | 121.194 | 159.256 | 0.023433 | 11.6415 | -0.12573 | 0.062294
CH_PLANT | Tampines 1 | 1/8/2024 3:00:00 am | 0.10337 | 248.875 | 162.1848 | 0.024667 | 8.6229 | -0.1179 | 0.051746
CH_PLANT | Tampines 1 | 1/8/2024 4:00:00 am | 0.10337 | 134.2565 | 160.167 | 0.022583 | 12.1001 | -0.11933 | 0.045209
CH_PLANT | Tampines 1 | 1/8/2024 5:00:00 am | 0.10337 | 140.4328 | 159.955 | 0.0215 | 8.3245 | -0.13251 | 0.038586
CH_PLANT | Tampines 1 | 1/8/2024 6:00:00 am | 2.8605 | 140.6595 | 163.0452 | 1.192 | 9.7423 | -0.55642 | 0.030394
CH_PLANT | Tampines 1 | 1/8/2024 7:00:00 am | 382.921 | 141.4652 | 298.5412 | 71.062 | 0.71877 | -0.48945 | 0.024451
CH_PLANT | Tampines 1 | 1/8/2024 8:00:00 am | 210.5681 | 143.8553 | 271.85 | 42.7672 | 0.70324 | -0.32384 | 9.7405
CH_PLANT | Tampines 1 | 1/8/2024 9:00:00 am | 220.4561 | 140.671 | 164.7647 | 40.6946 | 0.70861 | -0.18545 | 1621.899
CH_PLANT | Tampines 1 | 1/8/2024 10:00:00 am | 217.8993 | 142.5722 | 1.6623 | 40.6721 | 0.69414 | 0.20734 | 1012.545
CH_PLANT | Tampines 1 | 1/8/2024 11:00:00 am | 221.179 | 142.0108 | 1.4982 | 40.6807 | 0.70578 | 0.58086 | 0.48901
CH_PLANT | Tampines 1 | 1/8/2024 12:00:00 pm | 244.9366 | 138.9657 | 278.581 | 41.0242 | 0.65144 | 1.3976 | 0.052207
CH_PLANT | Tampines 1 | 1/8/2024 1:00:00 pm | 250.8755 | 140.1183 | 149.3538 | 41.0311 | 0.64721 | 0.013006 | 0.055203
CH_PLANT | Tampines 1 | 1/8/2024 2:00:00 pm | 251.4543 | 137.84 | 160.7307 | 41.0917 | 0.63682 | -0.14062 | 0.054199
CH_PLANT | Tampines 1 | 1/8/2024 3:00:00 pm | 249.4768 | 139.6983 | 161.7633 | 41.0286 | 0.63863 | -0.14404 | 0.045992
CH_PLANT | Tampines 1 | 1/8/2024 4:00:00 pm | 255.8599 | 283.4212 | 160.2337 | 44.2278 | 0.63777 | -0.1109 | 0.043262
CH_PLANT | Tampines 1 | 1/8/2024 5:00:00 pm | 399.1808 | 246.3632 | 162.5527 | 72.3453 | 0.74366 | 0.081825 | 0.043262
CH_PLANT | Tampines 1 | 1/8/2024 6:00:00 pm | 231.4076 | 152.9748 | 161.0952 | 71.715 | 0.83632 | -0.11574 | 0.043262
CH_PLANT | Tampines 1 | 1/8/2024 6:00:00 pm | 325.3193 | 141.4663 | 161.5225 | 48.1943 | 0.71517 | -0.2866 | 0.043262
CH_PLANT | Tampines 1 | 1/8/2024 7:00:00 pm | 0.26734 | 138.5828 | 159.4928 | 0.90082 | 83.5189 | -0.2866 | 0.043262
CH_PLANT | Tampines 1 | 1/8/2024 8:00:00 pm | 0.005783 | 140.726 | 160.5523 | 0.0267 | 93.2616 | -0.2866 | 0.043262
CH_PLANT | Tampines 1 | 1/8/2024 9:00:00 pm | 0.005783 | 141.1152 | 159.5868 | 0.029 | 56.1047 | -0.067319 | 6.3709
CH_PLANT | Tampines 1 | 1/8/2024 10:00:00 pm | 0.046738 | 140.76 | 157.33 | 0.029 | 17.6902 | 0.034298 | 1553.082
CH_PLANT | Tampines 1 | 1/8/2024 11:00:00 pm | 0.056977 | 145.1577 | 158.5388 | 0.029 | 17.1311 | 0.034298 | 900.5404
CH_PLANT | Tampines 1 | 2/8/2024 12:00:00 am | 0.056977 | 141.3635 | 1.6907 | 0.029 | 10.3691 | 0.034298 | 0.32157
CH_PLANT | Tampines 1 | 2/8/2024 1:00:00 am | 0.1023 | 143.7097 | 1.25 | 0.029 | 12.119 | 0.023504 | 0.039287
CH_PLANT | Tampines 1 | 2/8/2024 2:00:00 am | 0.11215 | 143.32 | 1.25 | 0.029 | 9.429 | 0.13675 | 0.039036
CH_PLANT | Tampines 1 | 2/8/2024 3:00:00 am | 0.11383 | 139.692 | 1.25 | 0.029 | 8.9298 | -0.14278 | 0.038355
CH_PLANT | Tampines 1 | 2/8/2024 4:00:00 am | 0.11383 | 0.83 | 1.25 | 0.029 | 10.0366 | -0.13003 | 0.038355
CH_PLANT | Tampines 1 | 2/8/2024 5:00:00 am | 0.11383 | 0.83 | 1.25 | 0.028833 | 7.0211 | -0.1194 | 0.034431
CH_PLANT | Tampines 1 | 2/8/2024 6:00:00 am | 5.6557 | 0.83 | 1.25 | 1.2127 | 9.1607 | 0.081239 | 0.027654
CH_PLANT | Tampines 1 | 2/8/2024 7:00:00 am | 381.8505 | 0.83 | 142.9307 | 70.9289 | 0.73104 | -0.2202 | 0.037175
CH_PLANT | Tampines 1 | 2/8/2024 8:00:00 am | 211.26 | 0.83 | 283.9762 | 42.8245 | 0.70969 | -0.33499 | 0.037677
CH_PLANT | Tampines 1 | 2/8/2024 9:00:00 am | 239.029 | 0.83 | 155.5683 | 40.9779 | 0.67503 | -0.33499 | 0.037677
CH_PLANT | Tampines 1 | 2/8/2024 10:00:00 am | 248.0222 | 0.83 | 159.8705 | 40.9816 | 0.65245 | 135.4711 | 0.035654
CH_PLANT | Tampines 1 | 2/8/2024 11:00:00 am | 251.2529 | 0.83 | 159.8542 | 41.0895 | 0.63801 | 135.4711 | 5.7509
CH_PLANT | Tampines 1 | 2/8/2024 12:00:00 pm | 251.8395 | 0.83 | 160.6118 | 41.0359 | 0.64496 | 135.4711 | 1944.854
CH_PLANT | Tampines 1 | 2/8/2024 1:00:00 pm | 249.4117 | 0.83 | 163.082 | 41.1324 | 0.64728 | 135.4711 | 983.0244
CH_PLANT | Tampines 1 | 2/8/2024 2:00:00 pm | 250.1121 | 0.83 | 159.8013 | 41.0387 | 0.64627 | 135.4711 | 0.32158
CH_PLANT | Tampines 1 | 2/8/2024 3:00:00 pm | 247.7325 | 0.83 | 161.696 | 41.1871 | 0.64315 | 135.4711 | 0.05447
CH_PLANT | Tampines 1 | 2/8/2024 4:00:00 pm | 256.2571 | 222.2117 | 161.149 | 41.0378 | 0.62559 | 65.4282 | 0.062073
CH_PLANT | Tampines 1 | 2/8/2024 5:00:00 pm | 252.5853 | 121.7788 | 158.0473 | 41.1095 | 0.63305 | -0.15394 | 0.052725
CH_PLANT | Tampines 1 | 2/8/2024 6:00:00 pm | 233.4623 | 140.3862 | 159.2922 | 41.106 | 0.63221 | -0.14521 | 0.050175
CH_PLANT | Tampines 1 | 2/8/2024 6:00:00 pm | 245.3633 | 141.6088 | 157.01 | 40.9408 | 0.78051 | 1.1826 | 0.050175
CH_PLANT | Tampines 1 | 2/8/2024 7:00:00 pm | 0 | 142.576 | 158.9154 | 0.95423 | 6.18 | -0.18117 | 862.9459
CH_PLANT | Tampines 1 | 2/8/2024 8:00:00 pm | 0 | 142.2313 | 1.803 | 0.023 | 6.18 | -0.49755 | 896.6569
CH_PLANT | Tampines 1 | 2/8/2024 9:00:00 pm | 0 | 142.9318 | 0.83 | 0.023 | 33.9825 | 1.3084 | 1038.853
CH_PLANT | Tampines 1 | 2/8/2024 10:00:00 pm | 0.016908 | 143.4013 | 0.83 | 0.023 | 26.6293 | 4.3057 | 1048.434
CH_PLANT | Tampines 1 | 2/8/2024 11:00:00 pm | 0.050723 | 143.1827 | 0.83 | 0.023 | 19.0397 | 7.5565 | 1038.186
CH_PLANT | Tampines 1 | 3/8/2024 12:00:00 am | 0.050723 | 141.9587 | 0.83 | 0.023 | 11.2898 | 9.063 | 1040.852
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.14088 | 139.8857 | 0.83 | 0.028 | 8.9551 | 9.6894 | 1058.503
CH_PLANT | Century Square | 29/7/2024 1:00:00 am | 0.14088 | 141.27 | 0.83 | 0.028 | 6.7642 | 12.821 | 1024.989
CH_PLANT | Century Square | 29/7/2024 2:00:00 am | 0.14088 | 141.7941 | 0.83 | 0.028 | 8.3708 | 15.5577 | 1065.603
CH_PLANT | Century Square | 29/7/2024 3:00:00 am | 0.14088 | 211.3907 | 0.83 | 0.028 | 8.4711 | 15.6908 | 1068.949
CH_PLANT | Century Square | 29/7/2024 4:00:00 am | 0.12797 | 125.0453 | 0.83 | 0.028 | 7.1738 | 25.7542 | 1064.135
CH_PLANT | Century Square | 29/7/2024 5:00:00 am | 0.088215 | 122.1157 | 0.83 | 0.028 | 10.6001 | -0.098259 | 870.7095
CH_PLANT | Century Square | 29/7/2024 6:00:00 am | 224.4682 | 134.7627 | 1.821 | 36.8521 | 4.5268 | -0.14402 | 900.9366
CH_PLANT | Century Square | 29/7/2024 7:00:00 am | 372.8486 | 142.0195 | 350.1997 | 70.7896 | 0.76155 | 0.33319 | 907.2243
CH_PLANT | Century Square | 29/7/2024 8:00:00 am | 227.3992 | 141.0818 | 281.2738 | 42.8775 | 0.68755 | -0.083678 | 893.1748
CH_PLANT | Century Square | 29/7/2024 9:00:00 am | 254.9916 | 144.3085 | 175.87 | 41.1297 | 0.62809 | -0.099753 | 1039.508
CH_PLANT | Century Square | 29/7/2024 10:00:00 am | 255.8372 | 143.05 | 160.6298 | 40.9786 | 0.6242 | 0.76645 | 1030.996
CH_PLANT | Century Square | 29/7/2024 11:00:00 am | 255.2364 | 144.1205 | 157.7287 | 41.0366 | 0.62774 | 6.3262 | 1043.581
CH_PLANT | Century Square | 29/7/2024 12:00:00 pm | 255.3587 | 144.5835 | 159.88 | 41.0893 | 0.63871 | 6.7394 | 1031.573
CH_PLANT | Century Square | 29/7/2024 1:00:00 pm | 252.129 | 265.318 | 160.2983 | 40.996 | 0.63407 | 12.6395 | 1058.812
CH_PLANT | Century Square | 29/7/2024 2:00:00 pm | 252.737 | 247.75 | 160.0222 | 40.9035 | 0.64034 | 18.9155 | 1063.401
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 256.828 | 127.7817 | 164.0948 | 41.1374 | 0.62836 | 20.4281 | 1057.548
CH_PLANT | Century Square | 29/7/2024 4:00:00 pm | 258.7526 | 280.6798 | 160.5053 | 40.9563 | 0.6121 | 21.0207 | 871.9294
CH_PLANT | Century Square | 29/7/2024 5:00:00 pm | 256.1333 | 235.2458 | 162.7955 | 41.0798 | 0.62325 | 28.5815 | 943.1224
CH_PLANT | Century Square | 29/7/2024 6:00:00 pm | 237.4005 | 168.3037 | 162.3 | 41.331 | 0.63779 | 21.9881 | 1033.666
CH_PLANT | Century Square | 29/7/2024 6:00:00 pm | 248.3295 | 145.1907 | 158.752 | 40.771 | 0.69522 | 0.029592 | 1056.056
CH_PLANT | Century Square | 29/7/2024 7:00:00 pm | 0 | 142.3572 | 1.8103 | 0.78508 | 2.3258 | -0.15671 | 1061.255
CH_PLANT | Century Square | 29/7/2024 8:00:00 pm | 0 | 143.2948 | 0.83 | 0.027 | 2.3258 | -0.10205 | 1041.611
CH_PLANT | Century Square | 29/7/2024 9:00:00 pm | 0 | 143.8213 | 0.83 | 0.027 | 60.3223 | -0.61256 | 1036.183
CH_PLANT | Century Square | 29/7/2024 10:00:00 pm | 0.030105 | 143.0695 | 0.83 | 0.027 | 28.2539 | -0.65419 | 1048.572
CH_PLANT | Century Square | 29/7/2024 11:00:00 pm | 0.051609 | 143.0172 | 0.83 | 0.027 | 11.6679 | -0.56783 | 1050.892
CH_PLANT | Century Square | 30/7/2024 12:00:00 am | 0.09993 | 144.2282 | 0.83 | 0.027 | 10.9317 | 1.5811 | 1067.901
CH_PLANT | Century Square | 30/7/2024 1:00:00 am | 0.10247 | 142.4952 | 0.83 | 0.027 | 9.8918 | 2.781 | 1066.451
CH_PLANT | Century Square | 30/7/2024 2:00:00 am | 0.10351 | 146.19 | 0.83 | 0.025433 | 7.504 | 4.1667 | 1164.098
CH_PLANT | Century Square | 30/7/2024 3:00:00 am | 0.10865 | 137.2217 | 0.83 | 0.025 | 9.4065 | 7.3829 | 1024.813
CH_PLANT | Century Square | 30/7/2024 4:00:00 am | 0.1146 | 0.83 | 0.83 | 0.025 | 6.7286 | 9.0097 | 1033.186
CH_PLANT | Century Square | 30/7/2024 5:00:00 am | 0.1146 | 0.83 | 0.83 | 0.025 | 7.1923 | 12.269 | 1037.898
CH_PLANT | Century Square | 30/7/2024 6:00:00 am | 7.0146 | 0.83 | 1.566 | 1.2336 | 8.6973 | 13.1164 | 1048.092
CH_PLANT | Century Square | 30/7/2024 7:00:00 am | 463.3467 | 0.83 | 257.5662 | 72.6787 | 0.91059 | 20.5579 | 1025.973
CH_PLANT | Century Square | 30/7/2024 8:00:00 am | 381.585 | 0.83 | 141.2028 | 72.349 | 0.73698 | -0.068321 | 1036.719
CH_PLANT | Century Square | 30/7/2024 9:00:00 am | 264.8494 | 0.83 | 159.5533 | 48.2704 | 0.71584 | -0.096173 | 1041.856
CH_PLANT | Century Square | 30/7/2024 10:00:00 am | 249.5523 | 0.82 | 160.7277 | 40.9349 | 0.64356 | 1.2825 | 1046.74
CH_PLANT | Century Square | 30/7/2024 11:00:00 am | 249.3424 | 0.82 | 161.6722 | 40.8956 | 0.64135 | -0.0037894 | 1051.684
CH_PLANT | Century Square | 30/7/2024 12:00:00 pm | 250.0159 | 0.82 | 161.3202 | 40.8453 | 0.63981 | -0.059149 | 1006.404
CH_PLANT | Century Square | 30/7/2024 1:00:00 pm | 249.2176 | 0.82 | 162.0658 | 40.8835 | 0.64295 | 2.6875 | 985.1463
CH_PLANT | Century Square | 30/7/2024 2:00:00 pm | 251.831 | 0.82 | 162.4497 | 40.993 | 0.63405 | 4.0545 | 1051.923
CH_PLANT | Century Square | 30/7/2024 3:00:00 pm | 252.5093 | 0.82 | 162.3155 | 40.877 | 0.65094 | 4.5709 | 1026.88
CH_PLANT | Century Square | 30/7/2024 4:00:00 pm | 254.2031 | 0.82 | 161.0215 | 40.8466 | 0.62832 | 9.3657 | 1033.496
CH_PLANT | Century Square | 30/7/2024 5:00:00 pm | 256.3384 | 0.82 | 158.8972 | 41.0233 | 0.63474 | 10.2887 | 1031.245
CH_PLANT | Century Square | 30/7/2024 6:00:00 pm | 234.9592 | 0.82 | 160.46 | 40.302 | 0.65138 | 12.2243 | 1031.94
CH_PLANT | Century Square | 30/7/2024 6:00:00 pm | 245.2163 | 0.82 | 160.8549 | 40.8383 | 1.5193 | 15.2955 | 1032.83
CH_PLANT | Century Square | 30/7/2024 7:00:00 pm | 0 | 0.82 | 1.8115 | 0.80522 | 50.4839 | 15.2891 | 1031.736
CH_PLANT | Century Square | 30/7/2024 8:00:00 pm | 0 | 0.82 | 0.83 | 0.029067 | 50.4839 | 15.1245 | 1047.3
CH_PLANT | Century Square | 30/7/2024 9:00:00 pm | 0 | 0.82 | 0.83 | 0.02285 | 58.4958 | -0.074615 | 1066.75
CH_PLANT | Century Square | 30/7/2024 10:00:00 pm | 0.011353 | 0.82 | 0.83 | 0.023167 | 33.253 | -0.14985 | 1059.366
CH_PLANT | Century Square | 30/7/2024 11:00:00 pm | 0.052398 | 0.82 | 0.83 | 0.023 | 15.5205 | -0.33667 | 859.2554
CH_PLANT | Century Square | 31/7/2024 12:00:00 am | 0.057491 | 0.82 | 0.83 | 0.023 | 11.1049 | -0.51807 | 924.161
CH_PLANT | Century Square | 31/7/2024 1:00:00 am | 0.10333 | 0.82 | 0.83 | 0.023 | 11.9385 | -0.53118 | 908.1718
CH_PLANT | Century Square | 31/7/2024 2:00:00 am | 0.10333 | 0.82 | 0.83 | 0.023 | 8.348 | 0.85671 | 925.0761
CH_PLANT | Century Square | 31/7/2024 3:00:00 am | 0.10333 | 0.82 | 0.83 | 0.023 | 10.1424 | 3.8126 | 992.4328
CH_PLANT | Century Square | 31/7/2024 4:00:00 am | 0.10333 | 0.82 | 0.83 | 0.023 | 7.7654 | 4.9252 | 1029.748
CH_PLANT | Century Square | 31/7/2024 5:00:00 am | 0.10667 | 0.82 | 0.83 | 0.023917 | 7.3475 | 519.5868 | 1046.874
CH_PLANT | Century Square | 31/7/2024 6:00:00 am | 2.5403 | 0.82 | 1.606 | 1.2107 | 9.0175 | 519.5868 | 1027.061
CH_PLANT | Century Square | 31/7/2024 7:00:00 am | 365.3462 | 0.82 | 247.0683 | 69.8127 | 0.70746 | 519.5868 | 1043.921
CH_PLANT | Century Square | 31/7/2024 8:00:00 am | 212.3759 | 0.82 | 144.425 | 40.7521 | 0.66427 | 519.5868 | 1726.136
CH_PLANT | Century Square | 31/7/2024 9:00:00 am | 249.7807 | 0.82 | 141.3698 | 40.903 | 0.63797 | 474.4282 | 1529.332
CH_PLANT | Century Square | 31/7/2024 10:00:00 am | 247.3195 | 0.82 | 153.9807 | 40.8578 | 0.64983 | 335.3918 | 857.3879
CH_PLANT | Century Square | 31/7/2024 11:00:00 am | 250.1599 | 0.82 | 161.1778 | 40.837 | 0.64628 | 162.0615 | 972.3392
CH_PLANT | Century Square | 31/7/2024 12:00:00 pm | 249.7924 | 0.82 | 160.195 | 40.8798 | 0.64557 | -0.16663 | 1018.362
CH_PLANT | Century Square | 31/7/2024 1:00:00 pm | 247.8874 | 0.82 | 163.2928 | 40.927 | 0.65392 | -0.16247 | 1038.569
CH_PLANT | Century Square | 31/7/2024 2:00:00 pm | 246.8563 | 0.82 | 162.1948 | 40.8882 | 0.65862 | 0.09563 | 1022.918
CH_PLANT | Century Square | 31/7/2024 3:00:00 pm | 247.3745 | 0.82 | 163.2433 | 40.9517 | 0.65602 | -0.38016 | 1011.85
CH_PLANT | Century Square | 31/7/2024 4:00:00 pm | 253.4572 | 0.82 | 164.0872 | 41.0271 | 0.63566 | -0.3892 | 1031.375
CH_PLANT | Century Square | 31/7/2024 5:00:00 pm | 250.997 | 0.82 | 297.1015 | 40.9806 | 0.63438 | 2.006 | 1020.958
CH_PLANT | Century Square | 31/7/2024 6:00:00 pm | 232.9099 | 0.82 | 392.14 | 42.115 | 0.63067 | 4.7174 | 1044.704
CH_PLANT | Century Square | 31/7/2024 6:00:00 pm | 255.1449 | 0.82 | 147.4105 | 40.8536 | 0.7504 | 10.5061 | 1039.928
CH_PLANT | Century Square | 31/7/2024 7:00:00 pm | 0 | 0.82 | 1.6167 | 0.79662 | 4.3689 | 10.778 | 1039.508
CH_PLANT | Century Square | 31/7/2024 8:00:00 pm | 0 | 0.82 | 1.6783 | 0.029 | 4.3689 | 10.8413 | 917.033
CH_PLANT | Century Square | 31/7/2024 9:00:00 pm | 0 | 0.82 | 315.7033 | 0.029 | 27.4066 | 11.3776 | 1043.856
CH_PLANT | Century Square | 31/7/2024 10:00:00 pm | 0.003336 | 0.82 | 269.4812 | 0.029 | 36.4171 | 12.0136 | 1068.608
CH_PLANT | Century Square | 31/7/2024 11:00:00 pm | 0.050039 | 0.82 | 194.1592 | 0.029 | 15.7932 | 12.0136 | 1062.827
CH_PLANT | Century Square | 1/8/2024 12:00:00 am | 0.06097 | 0.82 | 164.454 | 0.029 | 12.5621 | 13.5211 | 1061.97
CH_PLANT | Century Square | 1/8/2024 1:00:00 am | 0.10133 | 0.82 | 161.5215 | 0.029 | 12.1175 | -0.10711 | 1049.042
CH_PLANT | Century Square | 1/8/2024 2:00:00 am | 0.10133 | 0.82 | 162.4512 | 0.029 | 8.293 | -0.16377 | 1058.536
CH_PLANT | Century Square | 1/8/2024 3:00:00 am | 0.10133 | 0.82 | 163.0525 | 0.029 | 10.2453 | -0.26544 | 1069.365
CH_PLANT | Century Square | 1/8/2024 4:00:00 am | 0.11248 | 0.82 | 162.2298 | 0.029 | 7.0494 | -0.65973 | 1080.882
CH_PLANT | Century Square | 1/8/2024 5:00:00 am | 0.14652 | 0.82 | 161.6363 | 0.029 | 7.4736 | -0.75466 | 1054.089
CH_PLANT | Century Square | 1/8/2024 6:00:00 am | 5.331 | 0.82 | 161.6212 | 1.2184 | 8.4863 | -0.22711 | 1033.741
CH_PLANT | Century Square | 1/8/2024 7:00:00 am | 351.8589 | 0.82 | 159.6117 | 67.4144 | 0.70809 | 1.9337 | 1645.933
CH_PLANT | Century Square | 1/8/2024 8:00:00 am | 212.4667 | 0.82 | 163.45 | 40.6611 | 0.67958 | 2.7027 | 1089.653
CH_PLANT | Century Square | 1/8/2024 9:00:00 am | 210.0121 | 0.82 | 154.4307 | 40.472 | 0.67429 | 6.4673 | 1035.09
CH_PLANT | Century Square | 1/8/2024 10:00:00 am | 237.0269 | 0.82 | 1.6485 | 40.7071 | 0.64985 | 7.6585 | 1037.43
CH_PLANT | Century Square | 1/8/2024 11:00:00 am | 252.6357 | 0.82 | 0.83 | 40.8074 | 0.63741 | 9.1501 | 1046.247
CH_PLANT | Century Square | 1/8/2024 12:00:00 pm | 251.0287 | 0.82 | 0.83 | 40.9122 | 0.63806 | 11.7132 | 1048.535
CH_PLANT | Century Square | 1/8/2024 1:00:00 pm | 253.9387 | 0.82 | 0.83 | 40.9128 | 0.64486 | 16.0617 | 1057.161
CH_PLANT | Century Square | 1/8/2024 2:00:00 pm | 249.9102 | 0.82 | 0.83 | 40.9515 | 0.64904 | 19.4863 | 1053.772
CH_PLANT | Century Square | 1/8/2024 3:00:00 pm | 248.2321 | 0.82 | 0.83 | 40.9115 | 0.65838 | -0.13261 | 1061.198
CH_PLANT | Century Square | 1/8/2024 4:00:00 pm | 256.5224 | 0.82 | 0.82 | 44.5145 | 0.64225 | -0.15931 | 1067.24
CH_PLANT | Century Square | 1/8/2024 5:00:00 pm | 396.3681 | 0.82 | 0.82 | 72.1615 | 0.75068 | -0.15236 | 1080.798
CH_PLANT | Century Square | 1/8/2024 6:00:00 pm | 211.2007 | 0.82 | 0.82 | 71.379 | 1.2173 | -0.43905 | 864.3814
CH_PLANT | Century Square | 1/8/2024 6:00:00 pm | 323.2855 | 0.82 | 0.82 | 44.9245 | 0.76314 | -0.47467 | 1024.406
CH_PLANT | Century Square | 1/8/2024 7:00:00 pm | 0 | 0.82 | 0.82 | 0.75627 | 4.453 | -0.24711 | 1039.213
CH_PLANT | Century Square | 1/8/2024 8:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 3.4996 | 1053.893
CH_PLANT | Century Square | 1/8/2024 9:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 4.627 | 1045.208
CH_PLANT | Century Square | 1/8/2024 10:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.611
CH_PLANT | Century Square | 1/8/2024 11:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1028.992
CH_PLANT | Century Square | 2/8/2024 12:00:00 am | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.406
CH_PLANT | Century Square | 2/8/2024 1:00:00 am | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 8.8144 | 1051.324
CH_PLANT | Century Square | 2/8/2024 2:00:00 am | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 11.5816 | 1049.278
CH_PLANT | Century Square | 2/8/2024 3:00:00 am | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 15.2228 | 1055.082
CH_PLANT | Century Square | 2/8/2024 4:00:00 am | 0 | 0.82 | 0.82 | 0.026 | 4.453 | -0.094059 | 877.9323
CH_PLANT | Century Square | 2/8/2024 5:00:00 am | 0 | 0.82 | 0.82 | 0.026 | 17.1926 | -0.12636 | 884.2773
CH_PLANT | Century Square | 2/8/2024 6:00:00 am | 5.731 | 0.82 | 0.82 | 1.2471 | 51.037 | -0.022934 | 970.1237
CH_PLANT | Century Square | 2/8/2024 7:00:00 am | 453.2346 | 0.82 | 0.82 | 72.5447 | 0.69187 | -0.2911 | 1061.106
CH_PLANT | Century Square | 2/8/2024 8:00:00 am | 362.744 | 0.82 | 0.82 | 72.2521 | 0.74228 | -0.33163 | 1058.15
CH_PLANT | Century Square | 2/8/2024 9:00:00 am | 277.8152 | 0.82 | 0.82 | 53.7303 | 0.69685 | -0.32213 | 1056.86
CH_PLANT | Century Square | 2/8/2024 10:00:00 am | 248.9746 | 0.82 | 0.82 | 40.9114 | 0.65995 | -0.32213 | 1040.489
CH_PLANT | Century Square | 2/8/2024 11:00:00 am | 247.4081 | 0.82 | 0.82 | 40.9621 | 0.65312 | -0.22594 | 1033.822
CH_PLANT | Century Square | 2/8/2024 12:00:00 pm | 249.8414 | 0.82 | 0.82 | 40.9006 | 0.65033 | -0.059809 | 1071.282
CH_PLANT | Century Square | 2/8/2024 1:00:00 pm | 248.2441 | 0.82 | 0.82 | 40.934 | 0.65789 | -0.29741 | 1727.56
CH_PLANT | Century Square | 2/8/2024 2:00:00 pm | 246.6658 | 0.82 | 0.82 | 40.9187 | 0.65846 | -0.30991 | 1539.706
CH_PLANT | Century Square | 2/8/2024 3:00:00 pm | 247.5377 | 0.82 | 0.82 | 40.9878 | 0.65259 | -0.30991 | 1561.595
CH_PLANT | Century Square | 2/8/2024 4:00:00 pm | 250.6421 | 0.82 | 0.82 | 40.8562 | 0.64558 | -0.25927 | 1158.264
CH_PLANT | Century Square | 2/8/2024 5:00:00 pm | 248.7138 | 0.82 | 0.82 | 40.9364 | 0.64336 | 0.72283 | 1033.918
CH_PLANT | Century Square | 2/8/2024 6:00:00 pm | 224.9341 | 0.82 | 0.82 | 40.757 | 0.66113 | -0.040134 | 1032.46
CH_PLANT | Century Square | 2/8/2024 6:00:00 pm | 245.7537 | 0.82 | 0.82 | 40.7378 | 0.70649 | -0.16181 | 1046.441
CH_PLANT | Century Square | 2/8/2024 7:00:00 pm | 0 | 0.82 | 0.82 | 0.79742 | 1.9423 | -0.22997 | 1036.824
CH_PLANT | Century Square | 2/8/2024 8:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48001 | 1024.879
CH_PLANT | Century Square | 2/8/2024 9:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.56223 | 1042.816
CH_PLANT | Century Square | 2/8/2024 10:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48538 | 1045.783
CH_PLANT | Century Square | 2/8/2024 11:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1039.836
CH_PLANT | Century Square | 3/8/2024 12:00:00 am | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1043.321
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | White Sands | 29/7/2024 1:00:00 am | 0 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | White Sands | 29/7/2024 2:00:00 am | 0 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | White Sands | 29/7/2024 3:00:00 am | 0 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | White Sands | 29/7/2024 4:00:00 am | 0 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | White Sands | 29/7/2024 5:00:00 am | 0 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | White Sands | 29/7/2024 6:00:00 am | 5.731 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | White Sands | 29/7/2024 7:00:00 am | 453.2346 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | White Sands | 29/7/2024 8:00:00 am | 362.744 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | White Sands | 29/7/2024 9:00:00 am | 277.8152 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | White Sands | 29/7/2024 10:00:00 am | 248.9746 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | White Sands | 29/7/2024 11:00:00 am | 247.4081 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | White Sands | 29/7/2024 12:00:00 pm | 249.8414 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | White Sands | 29/7/2024 1:00:00 pm | 248.2441 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | White Sands | 29/7/2024 2:00:00 pm | 246.6658 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 247.5377 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | White Sands | 29/7/2024 4:00:00 pm | 250.6421 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | White Sands | 29/7/2024 5:00:00 pm | 248.7138 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | White Sands | 29/7/2024 6:00:00 pm | 224.9341 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | White Sands | 29/7/2024 6:00:00 pm | 245.7537 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | White Sands | 29/7/2024 7:00:00 pm | 0 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | White Sands | 29/7/2024 8:00:00 pm | 0 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | White Sands | 29/7/2024 9:00:00 pm | 0 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | White Sands | 29/7/2024 10:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | White Sands | 29/7/2024 11:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | White Sands | 30/7/2024 12:00:00 am | 0 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | White Sands | 30/7/2024 1:00:00 am | 128.9868 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | White Sands | 30/7/2024 2:00:00 am | 128.9167 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | White Sands | 30/7/2024 3:00:00 am | 128.8466 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | White Sands | 30/7/2024 4:00:00 am | 128.7765 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | White Sands | 30/7/2024 5:00:00 am | 128.7064 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | White Sands | 30/7/2024 6:00:00 am | 128.6362 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | White Sands | 30/7/2024 7:00:00 am | 128.5661 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | White Sands | 30/7/2024 8:00:00 am | 128.496 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | White Sands | 30/7/2024 9:00:00 am | 128.4259 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | White Sands | 30/7/2024 10:00:00 am | 128.3558 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | White Sands | 30/7/2024 11:00:00 am | 128.2857 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | White Sands | 30/7/2024 12:00:00 pm | 128.2156 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | White Sands | 30/7/2024 1:00:00 pm | 128.1455 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | White Sands | 30/7/2024 2:00:00 pm | 128.0754 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | White Sands | 30/7/2024 3:00:00 pm | 128.0053 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | White Sands | 30/7/2024 4:00:00 pm | 127.9352 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | White Sands | 30/7/2024 5:00:00 pm | 127.865 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | White Sands | 30/7/2024 6:00:00 pm | 127.7949 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | White Sands | 30/7/2024 6:00:00 pm | 127.7248 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | White Sands | 30/7/2024 7:00:00 pm | 127.6547 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | White Sands | 30/7/2024 8:00:00 pm | 127.5846 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | White Sands | 30/7/2024 9:00:00 pm | 127.5145 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | White Sands | 30/7/2024 10:00:00 pm | 127.4444 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | White Sands | 30/7/2024 11:00:00 pm | 127.3743 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | White Sands | 31/7/2024 12:00:00 am | 127.3042 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | White Sands | 31/7/2024 1:00:00 am | 127.2341 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | White Sands | 31/7/2024 2:00:00 am | 127.164 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | White Sands | 31/7/2024 3:00:00 am | 127.0938 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | White Sands | 31/7/2024 4:00:00 am | 127.0237 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | White Sands | 31/7/2024 5:00:00 am | 126.9536 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | White Sands | 31/7/2024 6:00:00 am | 126.8835 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | White Sands | 31/7/2024 7:00:00 am | 126.8134 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | White Sands | 31/7/2024 8:00:00 am | 126.7433 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | White Sands | 31/7/2024 9:00:00 am | 126.6732 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | White Sands | 31/7/2024 10:00:00 am | 126.6031 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | White Sands | 31/7/2024 11:00:00 am | 126.533 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | White Sands | 31/7/2024 12:00:00 pm | 126.4629 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | White Sands | 31/7/2024 1:00:00 pm | 126.3927 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | White Sands | 31/7/2024 2:00:00 pm | 126.3226 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | White Sands | 31/7/2024 3:00:00 pm | 126.2525 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | White Sands | 31/7/2024 4:00:00 pm | 126.1824 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | White Sands | 31/7/2024 5:00:00 pm | 126.1123 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | White Sands | 31/7/2024 6:00:00 pm | 126.0422 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | White Sands | 31/7/2024 6:00:00 pm | 125.9721 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | White Sands | 31/7/2024 7:00:00 pm | 125.902 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | White Sands | 31/7/2024 8:00:00 pm | 125.8319 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | White Sands | 31/7/2024 9:00:00 pm | 125.7618 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | White Sands | 31/7/2024 10:00:00 pm | 125.6917 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | White Sands | 31/7/2024 11:00:00 pm | 125.6215 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | White Sands | 1/8/2024 12:00:00 am | 125.5514 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | White Sands | 1/8/2024 1:00:00 am | 125.4813 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | White Sands | 1/8/2024 2:00:00 am | 125.4112 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | White Sands | 1/8/2024 3:00:00 am | 125.3411 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | White Sands | 1/8/2024 4:00:00 am | 125.271 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | White Sands | 1/8/2024 5:00:00 am | 125.2009 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | White Sands | 1/8/2024 6:00:00 am | 125.1308 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | White Sands | 1/8/2024 7:00:00 am | 125.0607 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | White Sands | 1/8/2024 8:00:00 am | 124.9906 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | White Sands | 1/8/2024 9:00:00 am | 124.9204 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | White Sands | 1/8/2024 10:00:00 am | 124.8503 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | White Sands | 1/8/2024 11:00:00 am | 124.7802 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | White Sands | 1/8/2024 12:00:00 pm | 124.7101 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | White Sands | 1/8/2024 1:00:00 pm | 124.64 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | White Sands | 1/8/2024 2:00:00 pm | 124.5699 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | White Sands | 1/8/2024 3:00:00 pm | 124.4998 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | White Sands | 1/8/2024 4:00:00 pm | 124.4297 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | White Sands | 1/8/2024 5:00:00 pm | 124.3596 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | White Sands | 1/8/2024 6:00:00 pm | 124.2895 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | White Sands | 1/8/2024 6:00:00 pm | 124.2194 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | White Sands | 1/8/2024 7:00:00 pm | 124.1492 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | White Sands | 1/8/2024 8:00:00 pm | 124.0791 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | White Sands | 1/8/2024 9:00:00 pm | 124.009 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | White Sands | 1/8/2024 10:00:00 pm | 123.9389 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | White Sands | 1/8/2024 11:00:00 pm | 123.8688 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | White Sands | 2/8/2024 12:00:00 am | 123.7987 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | White Sands | 2/8/2024 1:00:00 am | 123.7286 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | White Sands | 2/8/2024 2:00:00 am | 123.6585 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | White Sands | 2/8/2024 3:00:00 am | 123.5884 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | White Sands | 2/8/2024 4:00:00 am | 123.5183 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | White Sands | 2/8/2024 5:00:00 am | 123.4482 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | White Sands | 2/8/2024 6:00:00 am | 123.378 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | White Sands | 2/8/2024 7:00:00 am | 123.3079 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | White Sands | 2/8/2024 8:00:00 am | 123.2378 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | White Sands | 2/8/2024 9:00:00 am | 123.1677 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | White Sands | 2/8/2024 10:00:00 am | 123.0976 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | White Sands | 2/8/2024 11:00:00 am | 123.0275 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | White Sands | 2/8/2024 12:00:00 pm | 122.9574 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | White Sands | 2/8/2024 1:00:00 pm | 122.8873 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | White Sands | 2/8/2024 2:00:00 pm | 122.8172 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | White Sands | 2/8/2024 3:00:00 pm | 122.7471 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766
CH_PLANT | White Sands | 2/8/2024 4:00:00 pm | 122.6769 | 131.7272 | 159.2118 | 41.079 | 0.62344 | -0.10051 | 0.040715
CH_PLANT | White Sands | 2/8/2024 5:00:00 pm | 122.6068 | 139.838 | 159.4572 | 40.9576 | 0.63158 | -0.10622 | 0.037693
CH_PLANT | White Sands | 2/8/2024 6:00:00 pm | 122.5367 | 142.3787 | 156.58 | 40.127 | 0.65917 | -0.059145 | 0.037693
CH_PLANT | White Sands | 2/8/2024 6:00:00 pm | 122.4666 | 142.9808 | 159.9854 | 40.9299 | 0.67922 | -0.084936 | 0.037693
CH_PLANT | White Sands | 2/8/2024 7:00:00 pm | 122.3965 | 141.9497 | 150.8555 | 40.908 | 0.69374 | -0.10325 | 0.035985
CH_PLANT | White Sands | 2/8/2024 8:00:00 pm | 122.3264 | 142.9197 | 138.1777 | 40.916 | 0.69775 | -0.10198 | 0.027444
CH_PLANT | White Sands | 2/8/2024 9:00:00 pm | 122.2563 | 141.6483 | 6.752 | 3.4926 | 83.086 | -0.10838 | 0.027444
CH_PLANT | White Sands | 2/8/2024 10:00:00 pm | 122.1862 | 137.604 | 0.84 | 0.027 | 100 | -0.11046 | 0.027444
CH_PLANT | White Sands | 2/8/2024 11:00:00 pm | 122.1161 | 140.7528 | 0.84 | 0.027 | 100 | -0.10784 | 5.3268
CH_PLANT | White Sands | 3/8/2024 12:00:00 am | 122.046 | 136.84 | 0.84 | 0.027 | 100 | -0.11336 | 1989.365
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.9759 | 141.4985 | 1.23 | 0.024 | 6.6646 | -0.11491 | 1021.944
CH_PLANT | Hougang Mall | 29/7/2024 1:00:00 am | 121.9057 | 0.83 | 1.23 | 0.024 | 7.3577 | -0.10588 | 0.549
CH_PLANT | Hougang Mall | 29/7/2024 2:00:00 am | 121.8356 | 0.83 | 1.23 | 0.024 | 5.7515 | -0.11082 | 0.032093
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 am | 121.7655 | 0.83 | 1.23 | 0.024 | 7.6403 | -0.13482 | 0.033581
CH_PLANT | Hougang Mall | 29/7/2024 4:00:00 am | 121.6954 | 0.83 | 1.23 | 0.024 | 6.4198 | -0.08407 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 5:00:00 am | 121.6253 | 0.83 | 1.23 | 0.024 | 5.6763 | -0.11678 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 6:00:00 am | 121.5552 | 0.83 | 145.6395 | 36.886 | 4.3894 | -0.11124 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 7:00:00 am | 121.4851 | 0.83 | 263.8778 | 70.8171 | 0.74909 | -0.11493 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 8:00:00 am | 121.415 | 0.83 | 143.6267 | 42.9785 | 0.68202 | -0.09018 | 0.020435
CH_PLANT | Hougang Mall | 29/7/2024 9:00:00 am | 121.3449 | 0.83 | 150.3923 | 40.7452 | 0.66066 | -0.10321 | 0.018327
CH_PLANT | Hougang Mall | 29/7/2024 10:00:00 am | 121.2748 | 0.83 | 157.531 | 40.9629 | 0.61277 | -0.11586 | 0.018327
CH_PLANT | Hougang Mall | 29/7/2024 11:00:00 am | 121.2047 | 0.83 | 159.9617 | 40.9678 | 0.61821 | -0.10567 | 0.018327
CH_PLANT | Hougang Mall | 29/7/2024 12:00:00 pm | 121.1345 | 0.83 | 160.407 | 41.0693 | 0.6237 | -0.093901 | 2.9502
CH_PLANT | Hougang Mall | 29/7/2024 1:00:00 pm | 121.0644 | 280.394 | 159.2295 | 41.0961 | 0.62318 | -0.14155 | 1566.063
CH_PLANT | Hougang Mall | 29/7/2024 2:00:00 pm | 120.9943 | 170.7897 | 160.1795 | 41.1538 | 0.63567 | -0.20497 | 1005.043
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.9242 | 142.1868 | 158.8533 | 41.0918 | 0.62736 | -0.077332 | 0.57226
CH_PLANT | Hougang Mall | 29/7/2024 4:00:00 pm | 120.8541 | 140.9953 | 154.8203 | 41.0734 | 0.60607 | -0.093229 | 0.061741
CH_PLANT | Hougang Mall | 29/7/2024 5:00:00 pm | 120.784 | 141.3117 | 158.0203 | 41.1464 | 0.60867 | -0.10299 | 0.074108
CH_PLANT | Hougang Mall | 29/7/2024 6:00:00 pm | 120.7139 | 142.0145 | 153.75 | 40.447 | 0.62025 | -0.10932 | 0.06796
CH_PLANT | Hougang Mall | 29/7/2024 6:00:00 pm | 120.6438 | 142.7058 | 158.8163 | 40.9356 | 0.65941 | -0.093705 | 0.061262
CH_PLANT | Hougang Mall | 29/7/2024 7:00:00 pm | 120.5737 | 139.9993 | 1.7892 | 1.4081 | 15.9491 | -0.092 | 0.056499
CH_PLANT | Hougang Mall | 29/7/2024 8:00:00 pm | 120.5036 | 139.8698 | 1.46 | 0.024 | 15.9491 | -0.10716 | 0.048864
CH_PLANT | Hougang Mall | 29/7/2024 9:00:00 pm | 120.4334 | 140.4943 | 314.0868 | 0.024 | 33.2896 | -0.10601 | 0.046605
CH_PLANT | Hougang Mall | 29/7/2024 10:00:00 pm | 120.3633 | 138.0458 | 192.8402 | 0.024 | 25.2073 | -0.097927 | 0.038783
CH_PLANT | Hougang Mall | 29/7/2024 11:00:00 pm | 120.2932 | 135.91 | 159.6322 | 0.024 | 16.7405 | -0.10611 | 0.029609
CH_PLANT | Hougang Mall | 30/7/2024 12:00:00 am | 120.2231 | 142.3993 | 158.3218 | 0.024 | 9.9003 | -0.13031 | 0.027377
CH_PLANT | Hougang Mall | 30/7/2024 1:00:00 am | 120.153 | 221.4172 | 158.681 | 0.024 | 12.0921 | -0.076295 | 7.2576
CH_PLANT | Hougang Mall | 30/7/2024 2:00:00 am | 120.0829 | 137.7345 | 159.248 | 0.024 | 8.3197 | -0.10132 | 1667.161
CH_PLANT | Hougang Mall | 30/7/2024 3:00:00 am | 120.0128 | 144.3753 | 159.9183 | 0.024 | 7.8482 | -0.11949 | 961.0121
CH_PLANT | Hougang Mall | 30/7/2024 4:00:00 am | 119.9427 | 143.3145 | 157.141 | 0.024 | 8.5625 | -0.11649 | 0.26549
CH_PLANT | Hougang Mall | 30/7/2024 5:00:00 am | 119.8726 | 142.7942 | 157.0072 | 0.024 | 6.1329 | -0.11532 | 0.048098
CH_PLANT | Hougang Mall | 30/7/2024 6:00:00 am | 119.8025 | 142.8697 | 157.6587 | 1.2388 | 7.6569 | -0.11547 | 0.052442
CH_PLANT | Hougang Mall | 30/7/2024 7:00:00 am | 119.7324 | 143.6523 | 155.0962 | 72.8287 | 0.67636 | -0.12133 | 0.052442
CH_PLANT | Hougang Mall | 30/7/2024 8:00:00 am | 119.6622 | 144.2565 | 153.18 | 50.2432 | 0.67834 | -0.11666 | 0.046237
CH_PLANT | Hougang Mall | 30/7/2024 9:00:00 am | 119.5921 | 143.0503 | 159.5095 | 41.0497 | 0.63689 | -0.11995 | 0.041877
CH_PLANT | Hougang Mall | 30/7/2024 10:00:00 am | 119.522 | 141.0682 | 1.8083 | 41.0843 | 0.62837 | -0.10615 | 0.037509
CH_PLANT | Hougang Mall | 30/7/2024 11:00:00 am | 119.4519 | 144.078 | 0.84 | 41.1265 | 0.62826 | -0.11515 | 0.037509
CH_PLANT | Hougang Mall | 30/7/2024 12:00:00 pm | 119.3818 | 145.99 | 0.84 | 40.9531 | 0.6288 | -0.13933 | 0.033416
CH_PLANT | Hougang Mall | 30/7/2024 1:00:00 pm | 119.3117 | 140.0364 | 0.84 | 41.0044 | 0.6375 | -0.096132 | 0.026347
CH_PLANT | Hougang Mall | 30/7/2024 2:00:00 pm | 119.2416 | 1.2 | 0.84 | 41.0585 | 0.6279 | -0.11237 | 0.026347
CH_PLANT | Hougang Mall | 30/7/2024 3:00:00 pm | 119.1715 | 1.2 | 0.84 | 41.0366 | 0.62291 | -0.11498 | 3.4504
CH_PLANT | Hougang Mall | 30/7/2024 4:00:00 pm | 119.1014 | 1.2 | 0.84 | 40.9098 | 0.61563 | -0.12037 | 1666.068
CH_PLANT | Hougang Mall | 30/7/2024 5:00:00 pm | 119.0313 | 1.2 | 0.84 | 41.0441 | 0.60789 | -0.12485 | 1008.752
CH_PLANT | Hougang Mall | 30/7/2024 6:00:00 pm | 118.9611 | 1.2 | 0.84 | 42.061 | 0.58872 | -0.12308 | 0.41415
CH_PLANT | Hougang Mall | 30/7/2024 6:00:00 pm | 118.891 | 1.2 | 0.84 | 40.914 | 0.68759 | -0.11821 | 0.049389
CH_PLANT | Hougang Mall | 30/7/2024 7:00:00 pm | 118.8209 | 1.2 | 0.84 | 1.4067 | 21.9641 | -0.11876 | 0.049699
CH_PLANT | Hougang Mall | 30/7/2024 8:00:00 pm | 118.7508 | 1.2 | 1.2152 | 0.027117 | 21.9641 | -0.1167 | 0.044414
CH_PLANT | Hougang Mall | 30/7/2024 9:00:00 pm | 118.6807 | 1.2 | 250.7245 | 0.029483 | 34.4065 | -0.16476 | 0.042329
CH_PLANT | Hougang Mall | 30/7/2024 10:00:00 pm | 118.6106 | 1.2 | 157.5758 | 0.02985 | 26.4288 | -0.086652 | 0.033989
CH_PLANT | Hougang Mall | 30/7/2024 11:00:00 pm | 118.5405 | 1.2 | 161.7642 | 0.03025 | 20.06 | -0.10189 | 0.001006
CH_PLANT | Hougang Mall | 31/7/2024 12:00:00 am | 118.4704 | 1.2 | 160.5303 | 0.03 | 10.5145 | -0.12355 | 0.001006
CH_PLANT | Hougang Mall | 31/7/2024 1:00:00 am | 118.4003 | 240.5975 | 159.9868 | 0.029833 | 10.3076 | -0.12614 | 0.001006
CH_PLANT | Hougang Mall | 31/7/2024 2:00:00 am | 118.3302 | 124.592 | 159.9677 | 0.029833 | 9.8666 | -0.12018 | 0.001006
CH_PLANT | Hougang Mall | 31/7/2024 3:00:00 am | 118.2601 | 136.7727 | 160.8637 | 0.028783 | 7.3602 | -0.11768 | 0.001006
CH_PLANT | Hougang Mall | 31/7/2024 4:00:00 am | 118.1899 | 131.7778 | 161.479 | 0.030667 | 9.7727 | -0.11644 | 0.001006
CH_PLANT | Hougang Mall | 31/7/2024 5:00:00 am | 118.1198 | 136.76 | 160.0555 | 0.030167 | 6.3896 | -0.11919 | 1009.799
CH_PLANT | Hougang Mall | 31/7/2024 6:00:00 am | 118.0497 | 140.0172 | 158.195 | 0.69977 | 7.0595 | -0.11297 | 1671.116
CH_PLANT | Hougang Mall | 31/7/2024 7:00:00 am | 117.9796 | 143.072 | 161.273 | 61.9782 | 0.66109 | -0.11959 | 1036.345
CH_PLANT | Hougang Mall | 31/7/2024 8:00:00 am | 117.9095 | 142.5625 | 162.53 | 45.4487 | 0.65936 | -0.10959 | 0.24878
CH_PLANT | Hougang Mall | 31/7/2024 9:00:00 am | 117.8394 | 142.6107 | 157.0676 | 41.1473 | 0.63108 | -0.10163 | 0.045289
CH_PLANT | Hougang Mall | 31/7/2024 10:00:00 am | 117.7693 | 145.348 | 2.1613 | 41.0763 | 0.64021 | -0.1187 | 0.044205
CH_PLANT | Hougang Mall | 31/7/2024 11:00:00 am | 117.6992 | 265.565 | 1.23 | 41.0747 | 0.63828 | -0.097798 | 0.044205
CH_PLANT | Hougang Mall | 31/7/2024 12:00:00 pm | 117.6291 | 239.71 | 1.23 | 41.1149 | 0.64312 | -0.12404 | 0.037228
CH_PLANT | Hougang Mall | 31/7/2024 1:00:00 pm | 117.559 | 143.6597 | 1.23 | 41.0748 | 0.64221 | -0.12684 | 0.032892
CH_PLANT | Hougang Mall | 31/7/2024 2:00:00 pm | 117.4889 | 244.3348 | 1.23 | 41.0344 | 0.64824 | -0.11608 | 0.032892
CH_PLANT | Hougang Mall | 31/7/2024 3:00:00 pm | 117.4187 | 128.6923 | 1.23 | 41.0037 | 0.6462 | -0.11577 | 0.032892
CH_PLANT | Hougang Mall | 31/7/2024 4:00:00 pm | 117.3486 | 141.4727 | 1.23 | 41.1388 | 0.621 | -0.11551 | 0.032892
CH_PLANT | Hougang Mall | 31/7/2024 5:00:00 pm | 117.2785 | 142.4573 | 1.23 | 41.1382 | 0.62535 | -0.10978 | 0.032892
CH_PLANT | Hougang Mall | 31/7/2024 6:00:00 pm | 117.2084 | 140.9642 | 1.23 | 40.495 | 0.63516 | -0.14848 | 0.032892
CH_PLANT | Hougang Mall | 31/7/2024 6:00:00 pm | 117.1383 | 143.3018 | 1.23 | 40.8738 | 0.73453 | -0.21519 | 5.9819
CH_PLANT | Hougang Mall | 31/7/2024 7:00:00 pm | 117.0682 | 141.8913 | 1.23 | 1.2019 | 38.2672 | -0.13602 | 2016.554
CH_PLANT | Hougang Mall | 31/7/2024 8:00:00 pm | 116.9981 | 142.2788 | 1.9288 | 0.022833 | 38.2672 | -0.10063 | 1028.995
CH_PLANT | Hougang Mall | 31/7/2024 9:00:00 pm | 116.928 | 140.1968 | 276.5095 | 0.025517 | 38.2672 | -0.11335 | 0.46443
CH_PLANT | Hougang Mall | 31/7/2024 10:00:00 pm | 116.8579 | 141.3907 | 145.4742 | 0.02915 | 47.7725 | -0.11737 | 0.087425
CH_PLANT | Hougang Mall | 31/7/2024 11:00:00 pm | 116.7878 | 140.492 | 156.0923 | 0.029017 | 25.0666 | -0.12104 | 0.093489
CH_PLANT | Hougang Mall | 1/8/2024 12:00:00 am | 116.7176 | 139.35 | 151.097 | 0.028836 | 12.7812 | -0.1182 | 0.082881
CH_PLANT | Hougang Mall | 1/8/2024 1:00:00 am | 116.6475 | 141.1839 | 155.9507 | 0.024383 | 11.9719 | -0.11327 | 0.071217
CH_PLANT | Hougang Mall | 1/8/2024 2:00:00 am | 116.5774 | 121.194 | 159.256 | 0.023433 | 11.6415 | -0.12573 | 0.062294
CH_PLANT | Hougang Mall | 1/8/2024 3:00:00 am | 116.5073 | 248.875 | 162.1848 | 0.024667 | 8.6229 | -0.1179 | 0.051746
CH_PLANT | Hougang Mall | 1/8/2024 4:00:00 am | 116.4372 | 134.2565 | 160.167 | 0.022583 | 12.1001 | -0.11933 | 0.045209
CH_PLANT | Hougang Mall | 1/8/2024 5:00:00 am | 116.3671 | 140.4328 | 159.955 | 0.0215 | 8.3245 | -0.13251 | 0.038586
CH_PLANT | Hougang Mall | 1/8/2024 6:00:00 am | 116.297 | 140.6595 | 163.0452 | 1.192 | 9.7423 | -0.55642 | 0.030394
CH_PLANT | Hougang Mall | 1/8/2024 7:00:00 am | 116.2269 | 141.4652 | 298.5412 | 71.062 | 0.71877 | -0.48945 | 0.024451
CH_PLANT | Hougang Mall | 1/8/2024 8:00:00 am | 116.1568 | 143.8553 | 271.85 | 42.7672 | 0.70324 | -0.32384 | 9.7405
CH_PLANT | Hougang Mall | 1/8/2024 9:00:00 am | 116.0867 | 140.671 | 164.7647 | 40.6946 | 0.70861 | -0.18545 | 1621.899
CH_PLANT | Hougang Mall | 1/8/2024 10:00:00 am | 116.0166 | 142.5722 | 1.6623 | 40.6721 | 0.69414 | 0.20734 | 1012.545
CH_PLANT | Hougang Mall | 1/8/2024 11:00:00 am | 115.9464 | 142.0108 | 1.4982 | 40.6807 | 0.70578 | 0.58086 | 0.48901
CH_PLANT | Hougang Mall | 1/8/2024 12:00:00 pm | 115.8763 | 138.9657 | 278.581 | 41.0242 | 0.65144 | 1.3976 | 0.052207
CH_PLANT | Hougang Mall | 1/8/2024 1:00:00 pm | 115.8062 | 140.1183 | 149.3538 | 41.0311 | 0.64721 | 0.013006 | 0.055203
CH_PLANT | Hougang Mall | 1/8/2024 2:00:00 pm | 115.7361 | 137.84 | 160.7307 | 41.0917 | 0.63682 | -0.14062 | 0.054199
CH_PLANT | Hougang Mall | 1/8/2024 3:00:00 pm | 115.666 | 139.6983 | 161.7633 | 41.0286 | 0.63863 | -0.14404 | 0.045992
CH_PLANT | Hougang Mall | 1/8/2024 4:00:00 pm | 115.5959 | 283.4212 | 160.2337 | 44.2278 | 0.63777 | -0.1109 | 0.043262
CH_PLANT | Hougang Mall | 1/8/2024 5:00:00 pm | 115.5258 | 246.3632 | 162.5527 | 72.3453 | 0.74366 | 0.081825 | 0.043262
CH_PLANT | Hougang Mall | 1/8/2024 6:00:00 pm | 115.4557 | 152.9748 | 161.0952 | 71.715 | 0.83632 | -0.11574 | 0.043262
CH_PLANT | Hougang Mall | 1/8/2024 6:00:00 pm | 115.3856 | 141.4663 | 161.5225 | 48.1943 | 0.71517 | -0.2866 | 0.043262
CH_PLANT | Hougang Mall | 1/8/2024 7:00:00 pm | 115.3155 | 138.5828 | 159.4928 | 0.90082 | 83.5189 | -0.2866 | 0.043262
CH_PLANT | Hougang Mall | 1/8/2024 8:00:00 pm | 115.2453 | 140.726 | 160.5523 | 0.0267 | 93.2616 | -0.2866 | 0.043262
CH_PLANT | Hougang Mall | 1/8/2024 9:00:00 pm | 115.1752 | 141.1152 | 159.5868 | 0.029 | 56.1047 | -0.067319 | 6.3709
CH_PLANT | Hougang Mall | 1/8/2024 10:00:00 pm | 115.1051 | 140.76 | 157.33 | 0.029 | 17.6902 | 0.034298 | 1553.082
CH_PLANT | Hougang Mall | 1/8/2024 11:00:00 pm | 115.035 | 145.1577 | 158.5388 | 0.029 | 17.1311 | 0.034298 | 900.5404
CH_PLANT | Hougang Mall | 2/8/2024 12:00:00 am | 114.9649 | 141.3635 | 1.6907 | 0.029 | 10.3691 | 0.034298 | 0.32157
CH_PLANT | Hougang Mall | 2/8/2024 1:00:00 am | 114.8948 | 143.7097 | 1.25 | 0.029 | 12.119 | 0.023504 | 0.039287
CH_PLANT | Hougang Mall | 2/8/2024 2:00:00 am | 114.8247 | 143.32 | 1.25 | 0.029 | 9.429 | 0.13675 | 0.039036
CH_PLANT | Hougang Mall | 2/8/2024 3:00:00 am | 114.7546 | 139.692 | 1.25 | 0.029 | 8.9298 | -0.14278 | 0.038355
CH_PLANT | Hougang Mall | 2/8/2024 4:00:00 am | 114.6845 | 0.83 | 1.25 | 0.029 | 10.0366 | -0.13003 | 0.038355
CH_PLANT | Hougang Mall | 2/8/2024 5:00:00 am | 114.6144 | 0.83 | 1.25 | 0.028833 | 7.0211 | -0.1194 | 0.034431
CH_PLANT | Hougang Mall | 2/8/2024 6:00:00 am | 114.5443 | 0.83 | 1.25 | 1.2127 | 9.1607 | 0.081239 | 0.027654
CH_PLANT | Hougang Mall | 2/8/2024 7:00:00 am | 114.4741 | 0.83 | 142.9307 | 70.9289 | 0.73104 | -0.2202 | 0.037175
CH_PLANT | Hougang Mall | 2/8/2024 8:00:00 am | 114.404 | 0.83 | 283.9762 | 42.8245 | 0.70969 | -0.33499 | 0.037677
CH_PLANT | Hougang Mall | 2/8/2024 9:00:00 am | 114.3339 | 0.83 | 155.5683 | 40.9779 | 0.67503 | -0.33499 | 0.037677
CH_PLANT | Hougang Mall | 2/8/2024 10:00:00 am | 114.2638 | 0.83 | 159.8705 | 40.9816 | 0.65245 | 135.4711 | 0.035654
CH_PLANT | Hougang Mall | 2/8/2024 11:00:00 am | 114.1937 | 0.83 | 159.8542 | 41.0895 | 0.63801 | 135.4711 | 5.7509
CH_PLANT | Hougang Mall | 2/8/2024 12:00:00 pm | 114.1236 | 0.83 | 160.6118 | 41.0359 | 0.64496 | 135.4711 | 1944.854
CH_PLANT | Hougang Mall | 2/8/2024 1:00:00 pm | 114.0535 | 0.83 | 163.082 | 41.1324 | 0.64728 | 135.4711 | 983.0244
CH_PLANT | Hougang Mall | 2/8/2024 2:00:00 pm | 113.9834 | 0.83 | 159.8013 | 41.0387 | 0.64627 | 135.4711 | 0.32158
CH_PLANT | Hougang Mall | 2/8/2024 3:00:00 pm | 113.9133 | 0.83 | 161.696 | 41.1871 | 0.64315 | 135.4711 | 0.05447
CH_PLANT | Hougang Mall | 2/8/2024 4:00:00 pm | 113.8432 | 222.2117 | 161.149 | 41.0378 | 0.62559 | 65.4282 | 0.062073
CH_PLANT | Hougang Mall | 2/8/2024 5:00:00 pm | 113.7731 | 121.7788 | 158.0473 | 41.1095 | 0.63305 | -0.15394 | 0.052725
CH_PLANT | Hougang Mall | 2/8/2024 6:00:00 pm | 113.7029 | 140.3862 | 159.2922 | 41.106 | 0.63221 | -0.14521 | 0.050175
CH_PLANT | Hougang Mall | 2/8/2024 6:00:00 pm | 113.6328 | 141.6088 | 157.01 | 40.9408 | 0.78051 | 1.1826 | 0.050175
CH_PLANT | Hougang Mall | 2/8/2024 7:00:00 pm | 113.5627 | 142.576 | 158.9154 | 0.95423 | 6.18 | -0.18117 | 862.9459
CH_PLANT | Hougang Mall | 2/8/2024 8:00:00 pm | 113.4926 | 142.2313 | 1.803 | 0.023 | 6.18 | -0.49755 | 896.6569
CH_PLANT | Hougang Mall | 2/8/2024 9:00:00 pm | 113.4225 | 142.9318 | 0.83 | 0.023 | 33.9825 | 1.3084 | 1038.853
CH_PLANT | Hougang Mall | 2/8/2024 10:00:00 pm | 113.3524 | 143.4013 | 0.83 | 0.023 | 26.6293 | 4.3057 | 1048.434
CH_PLANT | Hougang Mall | 2/8/2024 11:00:00 pm | 113.2823 | 143.1827 | 0.83 | 0.023 | 19.0397 | 7.5565 | 1038.186
CH_PLANT | Hougang Mall | 3/8/2024 12:00:00 am | 113.2122 | 141.9587 | 0.83 | 0.023 | 11.2898 | 9.063 | 1040.852
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 113.1421 | 139.8857 | 0.83 | 0.028 | 8.9551 | 9.6894 | 1058.503
CH_PLANT | Waterway Point | 29/7/2024 1:00:00 am | 113.072 | 141.27 | 0.83 | 0.028 | 6.7642 | 12.821 | 1024.989
CH_PLANT | Waterway Point | 29/7/2024 2:00:00 am | 113.0018 | 141.7941 | 0.83 | 0.028 | 8.3708 | 15.5577 | 1065.603
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 am | 112.9317 | 211.3907 | 0.83 | 0.028 | 8.4711 | 15.6908 | 1068.949
CH_PLANT | Waterway Point | 29/7/2024 4:00:00 am | 112.8616 | 125.0453 | 0.83 | 0.028 | 7.1738 | 25.7542 | 1064.135
CH_PLANT | Waterway Point | 29/7/2024 5:00:00 am | 112.7915 | 122.1157 | 0.83 | 0.028 | 10.6001 | -0.098259 | 870.7095
CH_PLANT | Waterway Point | 29/7/2024 6:00:00 am | 112.7214 | 134.7627 | 1.821 | 36.8521 | 4.5268 | -0.14402 | 900.9366
CH_PLANT | Waterway Point | 29/7/2024 7:00:00 am | 112.6513 | 142.0195 | 350.1997 | 70.7896 | 0.76155 | 0.33319 | 907.2243
CH_PLANT | Waterway Point | 29/7/2024 8:00:00 am | 112.5812 | 141.0818 | 281.2738 | 42.8775 | 0.68755 | -0.083678 | 893.1748
CH_PLANT | Waterway Point | 29/7/2024 9:00:00 am | 112.5111 | 144.3085 | 175.87 | 41.1297 | 0.62809 | -0.099753 | 1039.508
CH_PLANT | Waterway Point | 29/7/2024 10:00:00 am | 112.441 | 143.05 | 160.6298 | 40.9786 | 0.6242 | 0.76645 | 1030.996
CH_PLANT | Waterway Point | 29/7/2024 11:00:00 am | 112.3709 | 144.1205 | 157.7287 | 41.0366 | 0.62774 | 6.3262 | 1043.581
CH_PLANT | Waterway Point | 29/7/2024 12:00:00 pm | 112.3008 | 144.5835 | 159.88 | 41.0893 | 0.63871 | 6.7394 | 1031.573
CH_PLANT | Waterway Point | 29/7/2024 1:00:00 pm | 112.2306 | 265.318 | 160.2983 | 40.996 | 0.63407 | 12.6395 | 1058.812
CH_PLANT | Waterway Point | 29/7/2024 2:00:00 pm | 112.1605 | 247.75 | 160.0222 | 40.9035 | 0.64034 | 18.9155 | 1063.401
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.0904 | 127.7817 | 164.0948 | 41.1374 | 0.62836 | 20.4281 | 1057.548
CH_PLANT | Waterway Point | 29/7/2024 4:00:00 pm | 112.0203 | 280.6798 | 160.5053 | 40.9563 | 0.6121 | 21.0207 | 871.9294
CH_PLANT | Waterway Point | 29/7/2024 5:00:00 pm | 111.9502 | 235.2458 | 162.7955 | 41.0798 | 0.62325 | 28.5815 | 943.1224
CH_PLANT | Waterway Point | 29/7/2024 6:00:00 pm | 111.8801 | 168.3037 | 162.3 | 41.331 | 0.63779 | 21.9881 | 1033.666
CH_PLANT | Waterway Point | 29/7/2024 6:00:00 pm | 111.81 | 145.1907 | 158.752 | 40.771 | 0.69522 | 0.029592 | 1056.056
CH_PLANT | Waterway Point | 29/7/2024 7:00:00 pm | 111.7399 | 142.3572 | 1.8103 | 0.78508 | 2.3258 | -0.15671 | 1061.255
CH_PLANT | Waterway Point | 29/7/2024 8:00:00 pm | 111.6698 | 143.2948 | 0.83 | 0.027 | 2.3258 | -0.10205 | 1041.611
CH_PLANT | Waterway Point | 29/7/2024 9:00:00 pm | 111.5997 | 143.8213 | 0.83 | 0.027 | 60.3223 | -0.61256 | 1036.183
CH_PLANT | Waterway Point | 29/7/2024 10:00:00 pm | 111.5296 | 143.0695 | 0.83 | 0.027 | 28.2539 | -0.65419 | 1048.572
CH_PLANT | Waterway Point | 29/7/2024 11:00:00 pm | 111.4594 | 143.0172 | 0.83 | 0.027 | 11.6679 | -0.56783 | 1050.892
CH_PLANT | Waterway Point | 30/7/2024 12:00:00 am | 111.3893 | 144.2282 | 0.83 | 0.027 | 10.9317 | 1.5811 | 1067.901
CH_PLANT | Waterway Point | 30/7/2024 1:00:00 am | 111.3192 | 142.4952 | 0.83 | 0.027 | 9.8918 | 2.781 | 1066.451
CH_PLANT | Waterway Point | 30/7/2024 2:00:00 am | 111.2491 | 146.19 | 0.83 | 0.025433 | 7.504 | 4.1667 | 1164.098
CH_PLANT | Waterway Point | 30/7/2024 3:00:00 am | 111.179 | 137.2217 | 0.83 | 0.025 | 9.4065 | 7.3829 | 1024.813
CH_PLANT | Waterway Point | 30/7/2024 4:00:00 am | 111.1089 | 0.83 | 0.83 | 0.025 | 6.7286 | 9.0097 | 1033.186
CH_PLANT | Waterway Point | 30/7/2024 5:00:00 am | 111.0388 | 0.83 | 0.83 | 0.025 | 7.1923 | 12.269 | 1037.898
CH_PLANT | Waterway Point | 30/7/2024 6:00:00 am | 110.9687 | 0.83 | 1.566 | 1.2336 | 8.6973 | 13.1164 | 1048.092
CH_PLANT | Waterway Point | 30/7/2024 7:00:00 am | 110.8986 | 0.83 | 257.5662 | 72.6787 | 0.91059 | 20.5579 | 1025.973
CH_PLANT | Waterway Point | 30/7/2024 8:00:00 am | 110.8285 | 0.83 | 141.2028 | 72.349 | 0.73698 | -0.068321 | 1036.719
CH_PLANT | Waterway Point | 30/7/2024 9:00:00 am | 110.7583 | 0.83 | 159.5533 | 48.2704 | 0.71584 | -0.096173 | 1041.856
CH_PLANT | Waterway Point | 30/7/2024 10:00:00 am | 110.6882 | 0.82 | 160.7277 | 40.9349 | 0.64356 | 1.2825 | 1046.74
CH_PLANT | Waterway Point | 30/7/2024 11:00:00 am | 110.6181 | 0.82 | 161.6722 | 40.8956 | 0.64135 | -0.0037894 | 1051.684
CH_PLANT | Waterway Point | 30/7/2024 12:00:00 pm | 110.548 | 0.82 | 161.3202 | 40.8453 | 0.63981 | -0.059149 | 1006.404
CH_PLANT | Waterway Point | 30/7/2024 1:00:00 pm | 110.4779 | 0.82 | 162.0658 | 40.8835 | 0.64295 | 2.6875 | 985.1463
CH_PLANT | Waterway Point | 30/7/2024 2:00:00 pm | 110.4078 | 0.82 | 162.4497 | 40.993 | 0.63405 | 4.0545 | 1051.923
CH_PLANT | Waterway Point | 30/7/2024 3:00:00 pm | 110.3377 | 0.82 | 162.3155 | 40.877 | 0.65094 | 4.5709 | 1026.88
CH_PLANT | Waterway Point | 30/7/2024 4:00:00 pm | 110.2676 | 0.82 | 161.0215 | 40.8466 | 0.62832 | 9.3657 | 1033.496
CH_PLANT | Waterway Point | 30/7/2024 5:00:00 pm | 110.1975 | 0.82 | 158.8972 | 41.0233 | 0.63474 | 10.2887 | 1031.245
CH_PLANT | Waterway Point | 30/7/2024 6:00:00 pm | 110.1274 | 0.82 | 160.46 | 40.302 | 0.65138 | 12.2243 | 1031.94
CH_PLANT | Waterway Point | 30/7/2024 6:00:00 pm | 110.0573 | 0.82 | 160.8549 | 40.8383 | 1.5193 | 15.2955 | 1032.83
CH_PLANT | Waterway Point | 30/7/2024 7:00:00 pm | 109.9871 | 0.82 | 1.8115 | 0.80522 | 50.4839 | 15.2891 | 1031.736
CH_PLANT | Waterway Point | 30/7/2024 8:00:00 pm | 109.917 | 0.82 | 0.83 | 0.029067 | 50.4839 | 15.1245 | 1047.3
CH_PLANT | Waterway Point | 30/7/2024 9:00:00 pm | 109.8469 | 0.82 | 0.83 | 0.02285 | 58.4958 | -0.074615 | 1066.75
CH_PLANT | Waterway Point | 30/7/2024 10:00:00 pm | 109.7768 | 0.82 | 0.83 | 0.023167 | 33.253 | -0.14985 | 1059.366
CH_PLANT | Waterway Point | 30/7/2024 11:00:00 pm | 109.7067 | 0.82 | 0.83 | 0.023 | 15.5205 | -0.33667 | 859.2554
CH_PLANT | Waterway Point | 31/7/2024 12:00:00 am | 109.6366 | 0.82 | 0.83 | 0.023 | 11.1049 | -0.51807 | 924.161
CH_PLANT | Waterway Point | 31/7/2024 1:00:00 am | 109.5665 | 0.82 | 0.83 | 0.023 | 11.9385 | -0.53118 | 908.1718
CH_PLANT | Waterway Point | 31/7/2024 2:00:00 am | 109.4964 | 0.82 | 0.83 | 0.023 | 8.348 | 0.85671 | 925.0761
CH_PLANT | Waterway Point | 31/7/2024 3:00:00 am | 109.4263 | 0.82 | 0.83 | 0.023 | 10.1424 | 3.8126 | 992.4328
CH_PLANT | Waterway Point | 31/7/2024 4:00:00 am | 109.3562 | 0.82 | 0.83 | 0.023 | 7.7654 | 4.9252 | 1029.748
CH_PLANT | Waterway Point | 31/7/2024 5:00:00 am | 109.286 | 0.82 | 0.83 | 0.023917 | 7.3475 | 519.5868 | 1046.874
CH_PLANT | Waterway Point | 31/7/2024 6:00:00 am | 109.2159 | 0.82 | 1.606 | 1.2107 | 9.0175 | 519.5868 | 1027.061
CH_PLANT | Waterway Point | 31/7/2024 7:00:00 am | 109.1458 | 0.82 | 247.0683 | 69.8127 | 0.70746 | 519.5868 | 1043.921
CH_PLANT | Waterway Point | 31/7/2024 8:00:00 am | 109.0757 | 0.82 | 144.425 | 40.7521 | 0.66427 | 519.5868 | 1726.136
CH_PLANT | Waterway Point | 31/7/2024 9:00:00 am | 109.0056 | 0.82 | 141.3698 | 40.903 | 0.63797 | 474.4282 | 1529.332
CH_PLANT | Waterway Point | 31/7/2024 10:00:00 am | 108.9355 | 0.82 | 153.9807 | 40.8578 | 0.64983 | 335.3918 | 857.3879
CH_PLANT | Waterway Point | 31/7/2024 11:00:00 am | 108.8654 | 0.82 | 161.1778 | 40.837 | 0.64628 | 162.0615 | 972.3392
CH_PLANT | Waterway Point | 31/7/2024 12:00:00 pm | 108.7953 | 0.82 | 160.195 | 40.8798 | 0.64557 | -0.16663 | 1018.362
CH_PLANT | Waterway Point | 31/7/2024 1:00:00 pm | 108.7252 | 0.82 | 163.2928 | 40.927 | 0.65392 | -0.16247 | 1038.569
CH_PLANT | Waterway Point | 31/7/2024 2:00:00 pm | 108.6551 | 0.82 | 162.1948 | 40.8882 | 0.65862 | 0.09563 | 1022.918
CH_PLANT | Waterway Point | 31/7/2024 3:00:00 pm | 108.585 | 0.82 | 163.2433 | 40.9517 | 0.65602 | -0.38016 | 1011.85
CH_PLANT | Waterway Point | 31/7/2024 4:00:00 pm | 108.5148 | 0.82 | 164.0872 | 41.0271 | 0.63566 | -0.3892 | 1031.375
CH_PLANT | Waterway Point | 31/7/2024 5:00:00 pm | 108.4447 | 0.82 | 297.1015 | 40.9806 | 0.63438 | 2.006 | 1020.958
CH_PLANT | Waterway Point | 31/7/2024 6:00:00 pm | 108.3746 | 0.82 | 392.14 | 42.115 | 0.63067 | 4.7174 | 1044.704
CH_PLANT | Waterway Point | 31/7/2024 6:00:00 pm | 108.3045 | 0.82 | 147.4105 | 40.8536 | 0.7504 | 10.5061 | 1039.928
CH_PLANT | Waterway Point | 31/7/2024 7:00:00 pm | 108.2344 | 0.82 | 1.6167 | 0.79662 | 4.3689 | 10.778 | 1039.508
CH_PLANT | Waterway Point | 31/7/2024 8:00:00 pm | 108.1643 | 0.82 | 1.6783 | 0.029 | 4.3689 | 10.8413 | 917.033
CH_PLANT | Waterway Point | 31/7/2024 9:00:00 pm | 108.0942 | 0.82 | 315.7033 | 0.029 | 27.4066 | 11.3776 | 1043.856
CH_PLANT | Waterway Point | 31/7/2024 10:00:00 pm | 108.0241 | 0.82 | 269.4812 | 0.029 | 36.4171 | 12.0136 | 1068.608
CH_PLANT | Waterway Point | 31/7/2024 11:00:00 pm | 107.954 | 0.82 | 194.1592 | 0.029 | 15.7932 | 12.0136 | 1062.827
CH_PLANT | Waterway Point | 1/8/2024 12:00:00 am | 107.8839 | 0.82 | 164.454 | 0.029 | 12.5621 | 13.5211 | 1061.97
CH_PLANT | Waterway Point | 1/8/2024 1:00:00 am | 107.8138 | 0.82 | 161.5215 | 0.029 | 12.1175 | -0.10711 | 1049.042
CH_PLANT | Waterway Point | 1/8/2024 2:00:00 am | 107.7436 | 0.82 | 162.4512 | 0.029 | 8.293 | -0.16377 | 1058.536
CH_PLANT | Waterway Point | 1/8/2024 3:00:00 am | 107.6735 | 0.82 | 163.0525 | 0.029 | 10.2453 | -0.26544 | 1069.365
CH_PLANT | Waterway Point | 1/8/2024 4:00:00 am | 107.6034 | 0.82 | 162.2298 | 0.029 | 7.0494 | -0.65973 | 1080.882
CH_PLANT | Waterway Point | 1/8/2024 5:00:00 am | 107.5333 | 0.82 | 161.6363 | 0.029 | 7.4736 | -0.75466 | 1054.089
CH_PLANT | Waterway Point | 1/8/2024 6:00:00 am | 107.4632 | 0.82 | 161.6212 | 1.2184 | 8.4863 | -0.22711 | 1033.741
CH_PLANT | Waterway Point | 1/8/2024 7:00:00 am | 107.3931 | 0.82 | 159.6117 | 67.4144 | 0.70809 | 1.9337 | 1645.933
CH_PLANT | Waterway Point | 1/8/2024 8:00:00 am | 107.323 | 0.82 | 163.45 | 40.6611 | 0.67958 | 2.7027 | 1089.653
CH_PLANT | Waterway Point | 1/8/2024 9:00:00 am | 107.2529 | 0.82 | 154.4307 | 40.472 | 0.67429 | 6.4673 | 1035.09
CH_PLANT | Waterway Point | 1/8/2024 10:00:00 am | 107.1828 | 0.82 | 1.6485 | 40.7071 | 0.64985 | 7.6585 | 1037.43
CH_PLANT | Waterway Point | 1/8/2024 11:00:00 am | 107.1127 | 0.82 | 0.83 | 40.8074 | 0.63741 | 9.1501 | 1046.247
CH_PLANT | Waterway Point | 1/8/2024 12:00:00 pm | 107.0425 | 0.82 | 0.83 | 40.9122 | 0.63806 | 11.7132 | 1048.535
CH_PLANT | Waterway Point | 1/8/2024 1:00:00 pm | 106.9724 | 0.82 | 0.83 | 40.9128 | 0.64486 | 16.0617 | 1057.161
CH_PLANT | Waterway Point | 1/8/2024 2:00:00 pm | 106.9023 | 0.82 | 0.83 | 40.9515 | 0.64904 | 19.4863 | 1053.772
CH_PLANT | Waterway Point | 1/8/2024 3:00:00 pm | 106.8322 | 0.82 | 0.83 | 40.9115 | 0.65838 | -0.13261 | 1061.198
CH_PLANT | Waterway Point | 1/8/2024 4:00:00 pm | 106.7621 | 0.82 | 0.82 | 44.5145 | 0.64225 | -0.15931 | 1067.24
CH_PLANT | Waterway Point | 1/8/2024 5:00:00 pm | 106.692 | 0.82 | 0.82 | 72.1615 | 0.75068 | -0.15236 | 1080.798
CH_PLANT | Waterway Point | 1/8/2024 6:00:00 pm | 106.6219 | 0.82 | 0.82 | 71.379 | 1.2173 | -0.43905 | 864.3814
CH_PLANT | Waterway Point | 1/8/2024 6:00:00 pm | 106.5518 | 0.82 | 0.82 | 44.9245 | 0.76314 | -0.47467 | 1024.406
CH_PLANT | Waterway Point | 1/8/2024 7:00:00 pm | 106.4817 | 0.82 | 0.82 | 0.75627 | 4.453 | -0.24711 | 1039.213
CH_PLANT | Waterway Point | 1/8/2024 8:00:00 pm | 106.4116 | 0.82 | 0.82 | 0.026 | 4.453 | 3.4996 | 1053.893
CH_PLANT | Waterway Point | 1/8/2024 9:00:00 pm | 106.3415 | 0.82 | 0.82 | 0.026 | 4.453 | 4.627 | 1045.208
CH_PLANT | Waterway Point | 1/8/2024 10:00:00 pm | 106.2713 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.611
CH_PLANT | Waterway Point | 1/8/2024 11:00:00 pm | 106.2012 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1028.992
CH_PLANT | Waterway Point | 2/8/2024 12:00:00 am | 106.1311 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.406
CH_PLANT | Waterway Point | 2/8/2024 1:00:00 am | 106.061 | 0.82 | 0.82 | 0.026 | 4.453 | 8.8144 | 1051.324
CH_PLANT | Waterway Point | 2/8/2024 2:00:00 am | 105.9909 | 0.82 | 0.82 | 0.026 | 4.453 | 11.5816 | 1049.278
CH_PLANT | Waterway Point | 2/8/2024 3:00:00 am | 105.9208 | 0.82 | 0.82 | 0.026 | 4.453 | 15.2228 | 1055.082
CH_PLANT | Waterway Point | 2/8/2024 4:00:00 am | 105.8507 | 0.82 | 0.82 | 0.026 | 4.453 | -0.094059 | 877.9323
CH_PLANT | Waterway Point | 2/8/2024 5:00:00 am | 105.7806 | 0.82 | 0.82 | 0.026 | 17.1926 | -0.12636 | 884.2773
CH_PLANT | Waterway Point | 2/8/2024 6:00:00 am | 105.7105 | 0.82 | 0.82 | 1.2471 | 51.037 | -0.022934 | 970.1237
CH_PLANT | Waterway Point | 2/8/2024 7:00:00 am | 105.6404 | 0.82 | 0.82 | 72.5447 | 0.69187 | -0.2911 | 1061.106
CH_PLANT | Waterway Point | 2/8/2024 8:00:00 am | 105.5702 | 0.82 | 0.82 | 72.2521 | 0.74228 | -0.33163 | 1058.15
CH_PLANT | Waterway Point | 2/8/2024 9:00:00 am | 105.5001 | 0.82 | 0.82 | 53.7303 | 0.69685 | -0.32213 | 1056.86
CH_PLANT | Waterway Point | 2/8/2024 10:00:00 am | 105.43 | 0.82 | 0.82 | 40.9114 | 0.65995 | -0.32213 | 1040.489
CH_PLANT | Waterway Point | 2/8/2024 11:00:00 am | 105.3599 | 0.82 | 0.82 | 40.9621 | 0.65312 | -0.22594 | 1033.822
CH_PLANT | Waterway Point | 2/8/2024 12:00:00 pm | 105.2898 | 0.82 | 0.82 | 40.9006 | 0.65033 | -0.059809 | 1071.282
CH_PLANT | Waterway Point | 2/8/2024 1:00:00 pm | 105.2197 | 0.82 | 0.82 | 40.934 | 0.65789 | -0.29741 | 1727.56
CH_PLANT | Waterway Point | 2/8/2024 2:00:00 pm | 105.1496 | 0.82 | 0.82 | 40.9187 | 0.65846 | -0.30991 | 1539.706
CH_PLANT | Waterway Point | 2/8/2024 3:00:00 pm | 105.0795 | 0.82 | 0.82 | 40.9878 | 0.65259 | -0.30991 | 1561.595
CH_PLANT | Waterway Point | 2/8/2024 4:00:00 pm | 105.0094 | 0.82 | 0.82 | 40.8562 | 0.64558 | -0.25927 | 1158.264
CH_PLANT | Waterway Point | 2/8/2024 5:00:00 pm | 104.9393 | 0.82 | 0.82 | 40.9364 | 0.64336 | 0.72283 | 1033.918
CH_PLANT | Waterway Point | 2/8/2024 6:00:00 pm | 104.8692 | 0.82 | 0.82 | 40.757 | 0.66113 | -0.040134 | 1032.46
CH_PLANT | Waterway Point | 2/8/2024 6:00:00 pm | 104.799 | 0.82 | 0.82 | 40.7378 | 0.70649 | -0.16181 | 1046.441
CH_PLANT | Waterway Point | 2/8/2024 7:00:00 pm | 104.7289 | 0.82 | 0.82 | 0.79742 | 1.9423 | -0.22997 | 1036.824
CH_PLANT | Waterway Point | 2/8/2024 8:00:00 pm | 104.6588 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48001 | 1024.879
CH_PLANT | Waterway Point | 2/8/2024 9:00:00 pm | 104.5887 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.56223 | 1042.816
CH_PLANT | Waterway Point | 2/8/2024 10:00:00 pm | 104.5186 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48538 | 1045.783
CH_PLANT | Waterway Point | 2/8/2024 11:00:00 pm | 104.4485 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1039.836
CH_PLANT | Waterway Point | 3/8/2024 12:00:00 am | 104.3784 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1043.321
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 104.3083 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 1:00:00 am | 104.2382 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 2:00:00 am | 104.1681 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 am | 104.098 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 4:00:00 am | 104.0278 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | North Point City (South Wing) | 29/7/2024 5:00:00 am | 103.9577 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | North Point City (South Wing) | 29/7/2024 6:00:00 am | 103.8876 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | North Point City (South Wing) | 29/7/2024 7:00:00 am | 103.8175 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | North Point City (South Wing) | 29/7/2024 8:00:00 am | 103.7474 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | North Point City (South Wing) | 29/7/2024 9:00:00 am | 103.6773 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | North Point City (South Wing) | 29/7/2024 10:00:00 am | 103.6072 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | North Point City (South Wing) | 29/7/2024 11:00:00 am | 103.5371 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | North Point City (South Wing) | 29/7/2024 12:00:00 pm | 103.467 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | North Point City (South Wing) | 29/7/2024 1:00:00 pm | 103.3969 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | North Point City (South Wing) | 29/7/2024 2:00:00 pm | 103.3267 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.2566 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | North Point City (South Wing) | 29/7/2024 4:00:00 pm | 103.1865 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | North Point City (South Wing) | 29/7/2024 5:00:00 pm | 103.1164 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | North Point City (South Wing) | 29/7/2024 6:00:00 pm | 103.0463 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | North Point City (South Wing) | 29/7/2024 6:00:00 pm | 102.9762 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | North Point City (South Wing) | 29/7/2024 7:00:00 pm | 102.9061 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | North Point City (South Wing) | 29/7/2024 8:00:00 pm | 102.836 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | North Point City (South Wing) | 29/7/2024 9:00:00 pm | 102.7659 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | North Point City (South Wing) | 29/7/2024 10:00:00 pm | 102.6958 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | North Point City (South Wing) | 29/7/2024 11:00:00 pm | 102.6257 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | North Point City (South Wing) | 30/7/2024 12:00:00 am | 102.5555 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 30/7/2024 1:00:00 am | 102.4854 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | North Point City (South Wing) | 30/7/2024 2:00:00 am | 102.4153 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 30/7/2024 3:00:00 am | 102.3452 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 30/7/2024 4:00:00 am | 102.2751 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 30/7/2024 5:00:00 am | 102.205 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | North Point City (South Wing) | 30/7/2024 6:00:00 am | 102.1349 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | North Point City (South Wing) | 30/7/2024 7:00:00 am | 102.0648 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | North Point City (South Wing) | 30/7/2024 8:00:00 am | 101.9947 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | North Point City (South Wing) | 30/7/2024 9:00:00 am | 101.9246 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | North Point City (South Wing) | 30/7/2024 10:00:00 am | 101.8544 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | North Point City (South Wing) | 30/7/2024 11:00:00 am | 101.7843 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | North Point City (South Wing) | 30/7/2024 12:00:00 pm | 101.7142 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | North Point City (South Wing) | 30/7/2024 1:00:00 pm | 101.6441 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | North Point City (South Wing) | 30/7/2024 2:00:00 pm | 101.574 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | North Point City (South Wing) | 30/7/2024 3:00:00 pm | 101.5039 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | North Point City (South Wing) | 30/7/2024 4:00:00 pm | 101.4338 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | North Point City (South Wing) | 30/7/2024 5:00:00 pm | 101.3637 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | North Point City (South Wing) | 30/7/2024 6:00:00 pm | 101.2936 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | North Point City (South Wing) | 30/7/2024 6:00:00 pm | 101.2235 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | North Point City (South Wing) | 30/7/2024 7:00:00 pm | 101.1534 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | North Point City (South Wing) | 30/7/2024 8:00:00 pm | 101.0832 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | North Point City (South Wing) | 30/7/2024 9:00:00 pm | 101.0131 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | North Point City (South Wing) | 30/7/2024 10:00:00 pm | 100.943 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | North Point City (South Wing) | 30/7/2024 11:00:00 pm | 100.8729 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | North Point City (South Wing) | 31/7/2024 12:00:00 am | 100.8028 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 31/7/2024 1:00:00 am | 100.7327 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 31/7/2024 2:00:00 am | 100.6626 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 31/7/2024 3:00:00 am | 100.5925 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 31/7/2024 4:00:00 am | 100.5224 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 31/7/2024 5:00:00 am | 100.4523 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 31/7/2024 6:00:00 am | 100.3822 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | North Point City (South Wing) | 31/7/2024 7:00:00 am | 100.312 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | North Point City (South Wing) | 31/7/2024 8:00:00 am | 100.2419 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | North Point City (South Wing) | 31/7/2024 9:00:00 am | 100.1718 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | North Point City (South Wing) | 31/7/2024 10:00:00 am | 100.1017 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | North Point City (South Wing) | 31/7/2024 11:00:00 am | 100.0316 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | North Point City (South Wing) | 31/7/2024 12:00:00 pm | 99.9615 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | North Point City (South Wing) | 31/7/2024 1:00:00 pm | 99.8914 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | North Point City (South Wing) | 31/7/2024 2:00:00 pm | 99.8213 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | North Point City (South Wing) | 31/7/2024 3:00:00 pm | 99.7512 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | North Point City (South Wing) | 31/7/2024 4:00:00 pm | 99.6811 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | North Point City (South Wing) | 31/7/2024 5:00:00 pm | 99.6109 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | North Point City (South Wing) | 31/7/2024 6:00:00 pm | 99.5408 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | North Point City (South Wing) | 31/7/2024 6:00:00 pm | 99.4707 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | North Point City (South Wing) | 31/7/2024 7:00:00 pm | 99.4006 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | North Point City (South Wing) | 31/7/2024 8:00:00 pm | 99.3305 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | North Point City (South Wing) | 31/7/2024 9:00:00 pm | 99.2604 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | North Point City (South Wing) | 31/7/2024 10:00:00 pm | 99.1903 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 31/7/2024 11:00:00 pm | 99.1202 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 1/8/2024 12:00:00 am | 99.0501 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | North Point City (South Wing) | 1/8/2024 1:00:00 am | 98.98 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | North Point City (South Wing) | 1/8/2024 2:00:00 am | 98.9099 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | North Point City (South Wing) | 1/8/2024 3:00:00 am | 98.8397 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | North Point City (South Wing) | 1/8/2024 4:00:00 am | 98.7696 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | North Point City (South Wing) | 1/8/2024 5:00:00 am | 98.6995 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | North Point City (South Wing) | 1/8/2024 6:00:00 am | 98.6294 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | North Point City (South Wing) | 1/8/2024 7:00:00 am | 98.5593 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | North Point City (South Wing) | 1/8/2024 8:00:00 am | 98.4892 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | North Point City (South Wing) | 1/8/2024 9:00:00 am | 98.4191 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | North Point City (South Wing) | 1/8/2024 10:00:00 am | 98.349 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | North Point City (South Wing) | 1/8/2024 11:00:00 am | 98.2789 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | North Point City (South Wing) | 1/8/2024 12:00:00 pm | 98.2088 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | North Point City (South Wing) | 1/8/2024 1:00:00 pm | 98.1387 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | North Point City (South Wing) | 1/8/2024 2:00:00 pm | 98.0685 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | North Point City (South Wing) | 1/8/2024 3:00:00 pm | 97.9984 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | North Point City (South Wing) | 1/8/2024 4:00:00 pm | 97.9283 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | North Point City (South Wing) | 1/8/2024 5:00:00 pm | 97.8582 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | North Point City (South Wing) | 1/8/2024 6:00:00 pm | 97.7881 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | North Point City (South Wing) | 1/8/2024 6:00:00 pm | 97.718 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | North Point City (South Wing) | 1/8/2024 7:00:00 pm | 97.6479 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | North Point City (South Wing) | 1/8/2024 8:00:00 pm | 97.5778 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | North Point City (South Wing) | 1/8/2024 9:00:00 pm | 97.5077 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | North Point City (South Wing) | 1/8/2024 10:00:00 pm | 97.4376 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | North Point City (South Wing) | 1/8/2024 11:00:00 pm | 97.3674 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | North Point City (South Wing) | 2/8/2024 12:00:00 am | 97.2973 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | North Point City (South Wing) | 2/8/2024 1:00:00 am | 97.2272 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | North Point City (South Wing) | 2/8/2024 2:00:00 am | 97.1571 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | North Point City (South Wing) | 2/8/2024 3:00:00 am | 97.087 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | North Point City (South Wing) | 2/8/2024 4:00:00 am | 97.0169 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | North Point City (South Wing) | 2/8/2024 5:00:00 am | 96.9468 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | North Point City (South Wing) | 2/8/2024 6:00:00 am | 96.8767 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | North Point City (South Wing) | 2/8/2024 7:00:00 am | 96.8066 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | North Point City (South Wing) | 2/8/2024 8:00:00 am | 96.7365 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | North Point City (South Wing) | 2/8/2024 9:00:00 am | 96.6664 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | North Point City (South Wing) | 2/8/2024 10:00:00 am | 96.5962 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | North Point City (South Wing) | 2/8/2024 11:00:00 am | 96.5261 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | North Point City (South Wing) | 2/8/2024 12:00:00 pm | 96.456 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | North Point City (South Wing) | 2/8/2024 1:00:00 pm | 96.3859 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | North Point City (South Wing) | 2/8/2024 2:00:00 pm | 96.3158 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | North Point City (South Wing) | 2/8/2024 3:00:00 pm | 96.2457 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766
CH_PLANT | North Point City (South Wing) | 2/8/2024 4:00:00 pm | 96.1756 | 131.7272 | 159.2118 | 41.079 | 0.62344 | -0.10051 | 0.040715
CH_PLANT | North Point City (South Wing) | 2/8/2024 5:00:00 pm | 96.1055 | 139.838 | 159.4572 | 40.9576 | 0.63158 | -0.10622 | 0.037693
CH_PLANT | North Point City (South Wing) | 2/8/2024 6:00:00 pm | 96.0354 | 142.3787 | 156.58 | 40.127 | 0.65917 | -0.059145 | 0.037693
CH_PLANT | North Point City (South Wing) | 2/8/2024 6:00:00 pm | 95.9653 | 142.9808 | 159.9854 | 40.9299 | 0.67922 | -0.084936 | 0.037693
CH_PLANT | North Point City (South Wing) | 2/8/2024 7:00:00 pm | 95.8951 | 141.9497 | 150.8555 | 40.908 | 0.69374 | -0.10325 | 0.035985
CH_PLANT | North Point City (South Wing) | 2/8/2024 8:00:00 pm | 95.825 | 142.9197 | 138.1777 | 40.916 | 0.69775 | -0.10198 | 0.027444
CH_PLANT | North Point City (South Wing) | 2/8/2024 9:00:00 pm | 95.7549 | 141.6483 | 6.752 | 3.4926 | 83.086 | -0.10838 | 0.027444
CH_PLANT | North Point City (South Wing) | 2/8/2024 10:00:00 pm | 95.6848 | 137.604 | 0.84 | 0.027 | 100 | -0.11046 | 0.027444
CH_PLANT | North Point City (South Wing) | 2/8/2024 11:00:00 pm | 95.6147 | 140.7528 | 0.84 | 0.027 | 100 | -0.10784 | 5.3268
CH_PLANT | North Point City (South Wing) | 3/8/2024 12:00:00 am | 95.5446 | 136.84 | 0.84 | 0.027 | 100 | -0.11336 | 1989.365
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.4745 | 141.4985 | 1.23 | 0.024 | 6.6646 | -0.11491 | 1021.944
CH_PLANT | The Centrepoint | 29/7/2024 1:00:00 am | 95.4044 | 0.83 | 1.23 | 0.024 | 7.3577 | -0.10588 | 0.549
CH_PLANT | The Centrepoint | 29/7/2024 2:00:00 am | 95.3343 | 0.83 | 1.23 | 0.024 | 5.7515 | -0.11082 | 0.032093
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 am | 95.2642 | 0.83 | 1.23 | 0.024 | 7.6403 | -0.13482 | 0.033581
CH_PLANT | The Centrepoint | 29/7/2024 4:00:00 am | 95.1941 | 0.83 | 1.23 | 0.024 | 6.4198 | -0.08407 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 5:00:00 am | 95.1239 | 0.83 | 1.23 | 0.024 | 5.6763 | -0.11678 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 6:00:00 am | 95.0538 | 0.83 | 145.6395 | 36.886 | 4.3894 | -0.11124 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 7:00:00 am | 94.9837 | 0.83 | 263.8778 | 70.8171 | 0.74909 | -0.11493 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 8:00:00 am | 94.9136 | 0.83 | 143.6267 | 42.9785 | 0.68202 | -0.09018 | 0.020435
CH_PLANT | The Centrepoint | 29/7/2024 9:00:00 am | 94.8435 | 0.83 | 150.3923 | 40.7452 | 0.66066 | -0.10321 | 0.018327
CH_PLANT | The Centrepoint | 29/7/2024 10:00:00 am | 94.7734 | 0.83 | 157.531 | 40.9629 | 0.61277 | -0.11586 | 0.018327
CH_PLANT | The Centrepoint | 29/7/2024 11:00:00 am | 94.7033 | 0.83 | 159.9617 | 40.9678 | 0.61821 | -0.10567 | 0.018327
CH_PLANT | The Centrepoint | 29/7/2024 12:00:00 pm | 94.6332 | 0.83 | 160.407 | 41.0693 | 0.6237 | -0.093901 | 2.9502
CH_PLANT | The Centrepoint | 29/7/2024 1:00:00 pm | 94.5631 | 280.394 | 159.2295 | 41.0961 | 0.62318 | -0.14155 | 1566.063
CH_PLANT | The Centrepoint | 29/7/2024 2:00:00 pm | 94.493 | 170.7897 | 160.1795 | 41.1538 | 0.63567 | -0.20497 | 1005.043
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.4229 | 142.1868 | 158.8533 | 41.0918 | 0.62736 | -0.077332 | 0.57226
CH_PLANT | The Centrepoint | 29/7/2024 4:00:00 pm | 94.3527 | 140.9953 | 154.8203 | 41.0734 | 0.60607 | -0.093229 | 0.061741
CH_PLANT | The Centrepoint | 29/7/2024 5:00:00 pm | 94.2826 | 141.3117 | 158.0203 | 41.1464 | 0.60867 | -0.10299 | 0.074108
CH_PLANT | The Centrepoint | 29/7/2024 6:00:00 pm | 94.2125 | 142.0145 | 153.75 | 40.447 | 0.62025 | -0.10932 | 0.06796
CH_PLANT | The Centrepoint | 29/7/2024 6:00:00 pm | 94.1424 | 142.7058 | 158.8163 | 40.9356 | 0.65941 | -0.093705 | 0.061262
CH_PLANT | The Centrepoint | 29/7/2024 7:00:00 pm | 94.0723 | 139.9993 | 1.7892 | 1.4081 | 15.9491 | -0.092 | 0.056499
CH_PLANT | The Centrepoint | 29/7/2024 8:00:00 pm | 94.0022 | 139.8698 | 1.46 | 0.024 | 15.9491 | -0.10716 | 0.048864
CH_PLANT | The Centrepoint | 29/7/2024 9:00:00 pm | 93.9321 | 140.4943 | 314.0868 | 0.024 | 33.2896 | -0.10601 | 0.046605
CH_PLANT | The Centrepoint | 29/7/2024 10:00:00 pm | 93.862 | 138.0458 | 192.8402 | 0.024 | 25.2073 | -0.097927 | 0.038783
CH_PLANT | The Centrepoint | 29/7/2024 11:00:00 pm | 93.7919 | 135.91 | 159.6322 | 0.024 | 16.7405 | -0.10611 | 0.029609
CH_PLANT | The Centrepoint | 30/7/2024 12:00:00 am | 93.7218 | 142.3993 | 158.3218 | 0.024 | 9.9003 | -0.13031 | 0.027377
CH_PLANT | The Centrepoint | 30/7/2024 1:00:00 am | 93.6516 | 221.4172 | 158.681 | 0.024 | 12.0921 | -0.076295 | 7.2576
CH_PLANT | The Centrepoint | 30/7/2024 2:00:00 am | 93.5815 | 137.7345 | 159.248 | 0.024 | 8.3197 | -0.10132 | 1667.161
CH_PLANT | The Centrepoint | 30/7/2024 3:00:00 am | 93.5114 | 144.3753 | 159.9183 | 0.024 | 7.8482 | -0.11949 | 961.0121
CH_PLANT | The Centrepoint | 30/7/2024 4:00:00 am | 93.4413 | 143.3145 | 157.141 | 0.024 | 8.5625 | -0.11649 | 0.26549
CH_PLANT | The Centrepoint | 30/7/2024 5:00:00 am | 93.3712 | 142.7942 | 157.0072 | 0.024 | 6.1329 | -0.11532 | 0.048098
CH_PLANT | The Centrepoint | 30/7/2024 6:00:00 am | 93.3011 | 142.8697 | 157.6587 | 1.2388 | 7.6569 | -0.11547 | 0.052442
CH_PLANT | The Centrepoint | 30/7/2024 7:00:00 am | 93.231 | 143.6523 | 155.0962 | 72.8287 | 0.67636 | -0.12133 | 0.052442
CH_PLANT | The Centrepoint | 30/7/2024 8:00:00 am | 93.1609 | 144.2565 | 153.18 | 50.2432 | 0.67834 | -0.11666 | 0.046237
CH_PLANT | The Centrepoint | 30/7/2024 9:00:00 am | 93.0908 | 143.0503 | 159.5095 | 41.0497 | 0.63689 | -0.11995 | 0.041877
CH_PLANT | The Centrepoint | 30/7/2024 10:00:00 am | 93.0207 | 141.0682 | 1.8083 | 41.0843 | 0.62837 | -0.10615 | 0.037509
CH_PLANT | The Centrepoint | 30/7/2024 11:00:00 am | 92.9506 | 144.078 | 0.84 | 41.1265 | 0.62826 | -0.11515 | 0.037509
CH_PLANT | The Centrepoint | 30/7/2024 12:00:00 pm | 92.8804 | 145.99 | 0.84 | 40.9531 | 0.6288 | -0.13933 | 0.033416
CH_PLANT | The Centrepoint | 30/7/2024 1:00:00 pm | 92.8103 | 140.0364 | 0.84 | 41.0044 | 0.6375 | -0.096132 | 0.026347
CH_PLANT | The Centrepoint | 30/7/2024 2:00:00 pm | 92.7402 | 1.2 | 0.84 | 41.0585 | 0.6279 | -0.11237 | 0.026347
CH_PLANT | The Centrepoint | 30/7/2024 3:00:00 pm | 92.6701 | 1.2 | 0.84 | 41.0366 | 0.62291 | -0.11498 | 3.4504
CH_PLANT | The Centrepoint | 30/7/2024 4:00:00 pm | 92.6 | 1.2 | 0.84 | 40.9098 | 0.61563 | -0.12037 | 1666.068
CH_PLANT | The Centrepoint | 30/7/2024 5:00:00 pm | 92.5299 | 1.2 | 0.84 | 41.0441 | 0.60789 | -0.12485 | 1008.752
CH_PLANT | The Centrepoint | 30/7/2024 6:00:00 pm | 92.4598 | 1.2 | 0.84 | 42.061 | 0.58872 | -0.12308 | 0.41415
CH_PLANT | The Centrepoint | 30/7/2024 6:00:00 pm | 92.3897 | 1.2 | 0.84 | 40.914 | 0.68759 | -0.11821 | 0.049389
CH_PLANT | The Centrepoint | 30/7/2024 7:00:00 pm | 92.3196 | 1.2 | 0.84 | 1.4067 | 21.9641 | -0.11876 | 0.049699
CH_PLANT | The Centrepoint | 30/7/2024 8:00:00 pm | 92.2495 | 1.2 | 1.2152 | 0.027117 | 21.9641 | -0.1167 | 0.044414
CH_PLANT | The Centrepoint | 30/7/2024 9:00:00 pm | 92.1793 | 1.2 | 250.7245 | 0.029483 | 34.4065 | -0.16476 | 0.042329
CH_PLANT | The Centrepoint | 30/7/2024 10:00:00 pm | 92.1092 | 1.2 | 157.5758 | 0.02985 | 26.4288 | -0.086652 | 0.033989
CH_PLANT | The Centrepoint | 30/7/2024 11:00:00 pm | 92.0391 | 1.2 | 161.7642 | 0.03025 | 20.06 | -0.10189 | 0.001006
CH_PLANT | The Centrepoint | 31/7/2024 12:00:00 am | 91.969 | 1.2 | 160.5303 | 0.03 | 10.5145 | -0.12355 | 0.001006
CH_PLANT | The Centrepoint | 31/7/2024 1:00:00 am | 91.8989 | 240.5975 | 159.9868 | 0.029833 | 10.3076 | -0.12614 | 0.001006
CH_PLANT | The Centrepoint | 31/7/2024 2:00:00 am | 91.8288 | 124.592 | 159.9677 | 0.029833 | 9.8666 | -0.12018 | 0.001006
CH_PLANT | The Centrepoint | 31/7/2024 3:00:00 am | 91.7587 | 136.7727 | 160.8637 | 0.028783 | 7.3602 | -0.11768 | 0.001006
CH_PLANT | The Centrepoint | 31/7/2024 4:00:00 am | 91.6886 | 131.7778 | 161.479 | 0.030667 | 9.7727 | -0.11644 | 0.001006
CH_PLANT | The Centrepoint | 31/7/2024 5:00:00 am | 91.6185 | 136.76 | 160.0555 | 0.030167 | 6.3896 | -0.11919 | 1009.799
CH_PLANT | The Centrepoint | 31/7/2024 6:00:00 am | 91.5484 | 140.0172 | 158.195 | 0.69977 | 7.0595 | -0.11297 | 1671.116
CH_PLANT | The Centrepoint | 31/7/2024 7:00:00 am | 91.4783 | 143.072 | 161.273 | 61.9782 | 0.66109 | -0.11959 | 1036.345
CH_PLANT | The Centrepoint | 31/7/2024 8:00:00 am | 91.4081 | 142.5625 | 162.53 | 45.4487 | 0.65936 | -0.10959 | 0.24878
CH_PLANT | The Centrepoint | 31/7/2024 9:00:00 am | 91.338 | 142.6107 | 157.0676 | 41.1473 | 0.63108 | -0.10163 | 0.045289
CH_PLANT | The Centrepoint | 31/7/2024 10:00:00 am | 91.2679 | 145.348 | 2.1613 | 41.0763 | 0.64021 | -0.1187 | 0.044205
CH_PLANT | The Centrepoint | 31/7/2024 11:00:00 am | 91.1978 | 265.565 | 1.23 | 41.0747 | 0.63828 | -0.097798 | 0.044205
CH_PLANT | The Centrepoint | 31/7/2024 12:00:00 pm | 91.1277 | 239.71 | 1.23 | 41.1149 | 0.64312 | -0.12404 | 0.037228
CH_PLANT | The Centrepoint | 31/7/2024 1:00:00 pm | 91.0576 | 143.6597 | 1.23 | 41.0748 | 0.64221 | -0.12684 | 0.032892
CH_PLANT | The Centrepoint | 31/7/2024 2:00:00 pm | 90.9875 | 244.3348 | 1.23 | 41.0344 | 0.64824 | -0.11608 | 0.032892
CH_PLANT | The Centrepoint | 31/7/2024 3:00:00 pm | 90.9174 | 128.6923 | 1.23 | 41.0037 | 0.6462 | -0.11577 | 0.032892
CH_PLANT | The Centrepoint | 31/7/2024 4:00:00 pm | 90.8473 | 141.4727 | 1.23 | 41.1388 | 0.621 | -0.11551 | 0.032892
CH_PLANT | The Centrepoint | 31/7/2024 5:00:00 pm | 90.7772 | 142.4573 | 1.23 | 41.1382 | 0.62535 | -0.10978 | 0.032892
CH_PLANT | The Centrepoint | 31/7/2024 6:00:00 pm | 90.7071 | 140.9642 | 1.23 | 40.495 | 0.63516 | -0.14848 | 0.032892
CH_PLANT | The Centrepoint | 31/7/2024 6:00:00 pm | 90.6369 | 143.3018 | 1.23 | 40.8738 | 0.73453 | -0.21519 | 5.9819
CH_PLANT | The Centrepoint | 31/7/2024 7:00:00 pm | 90.5668 | 141.8913 | 1.23 | 1.2019 | 38.2672 | -0.13602 | 2016.554
CH_PLANT | The Centrepoint | 31/7/2024 8:00:00 pm | 90.4967 | 142.2788 | 1.9288 | 0.022833 | 38.2672 | -0.10063 | 1028.995
CH_PLANT | The Centrepoint | 31/7/2024 9:00:00 pm | 90.4266 | 140.1968 | 276.5095 | 0.025517 | 38.2672 | -0.11335 | 0.46443
CH_PLANT | The Centrepoint | 31/7/2024 10:00:00 pm | 90.3565 | 141.3907 | 145.4742 | 0.02915 | 47.7725 | -0.11737 | 0.087425
CH_PLANT | The Centrepoint | 31/7/2024 11:00:00 pm | 90.2864 | 140.492 | 156.0923 | 0.029017 | 25.0666 | -0.12104 | 0.093489
CH_PLANT | The Centrepoint | 1/8/2024 12:00:00 am | 90.2163 | 139.35 | 151.097 | 0.028836 | 12.7812 | -0.1182 | 0.082881
CH_PLANT | The Centrepoint | 1/8/2024 1:00:00 am | 90.1462 | 141.1839 | 155.9507 | 0.024383 | 11.9719 | -0.11327 | 0.071217
CH_PLANT | The Centrepoint | 1/8/2024 2:00:00 am | 90.0761 | 121.194 | 159.256 | 0.023433 | 11.6415 | -0.12573 | 0.062294
CH_PLANT | The Centrepoint | 1/8/2024 3:00:00 am | 90.006 | 248.875 | 162.1848 | 0.024667 | 8.6229 | -0.1179 | 0.051746
CH_PLANT | The Centrepoint | 1/8/2024 4:00:00 am | 89.9358 | 134.2565 | 160.167 | 0.022583 | 12.1001 | -0.11933 | 0.045209
CH_PLANT | The Centrepoint | 1/8/2024 5:00:00 am | 89.8657 | 140.4328 | 159.955 | 0.0215 | 8.3245 | -0.13251 | 0.038586
CH_PLANT | The Centrepoint | 1/8/2024 6:00:00 am | 89.7956 | 140.6595 | 163.0452 | 1.192 | 9.7423 | -0.55642 | 0.030394
CH_PLANT | The Centrepoint | 1/8/2024 7:00:00 am | 89.7255 | 141.4652 | 298.5412 | 71.062 | 0.71877 | -0.48945 | 0.024451
CH_PLANT | The Centrepoint | 1/8/2024 8:00:00 am | 89.6554 | 143.8553 | 271.85 | 42.7672 | 0.70324 | -0.32384 | 9.7405
CH_PLANT | The Centrepoint | 1/8/2024 9:00:00 am | 89.5853 | 140.671 | 164.7647 | 40.6946 | 0.70861 | -0.18545 | 1621.899
CH_PLANT | The Centrepoint | 1/8/2024 10:00:00 am | 89.5152 | 142.5722 | 1.6623 | 40.6721 | 0.69414 | 0.20734 | 1012.545
CH_PLANT | The Centrepoint | 1/8/2024 11:00:00 am | 89.4451 | 142.0108 | 1.4982 | 40.6807 | 0.70578 | 0.58086 | 0.48901
CH_PLANT | The Centrepoint | 1/8/2024 12:00:00 pm | 89.375 | 138.9657 | 278.581 | 41.0242 | 0.65144 | 1.3976 | 0.052207
CH_PLANT | The Centrepoint | 1/8/2024 1:00:00 pm | 89.3049 | 140.1183 | 149.3538 | 41.0311 | 0.64721 | 0.013006 | 0.055203
CH_PLANT | The Centrepoint | 1/8/2024 2:00:00 pm | 89.2348 | 137.84 | 160.7307 | 41.0917 | 0.63682 | -0.14062 | 0.054199
CH_PLANT | The Centrepoint | 1/8/2024 3:00:00 pm | 89.1646 | 139.6983 | 161.7633 | 41.0286 | 0.63863 | -0.14404 | 0.045992
CH_PLANT | The Centrepoint | 1/8/2024 4:00:00 pm | 89.0945 | 283.4212 | 160.2337 | 44.2278 | 0.63777 | -0.1109 | 0.043262
CH_PLANT | The Centrepoint | 1/8/2024 5:00:00 pm | 89.0244 | 246.3632 | 162.5527 | 72.3453 | 0.74366 | 0.081825 | 0.043262
CH_PLANT | The Centrepoint | 1/8/2024 6:00:00 pm | 88.9543 | 152.9748 | 161.0952 | 71.715 | 0.83632 | -0.11574 | 0.043262
CH_PLANT | The Centrepoint | 1/8/2024 6:00:00 pm | 88.8842 | 141.4663 | 161.5225 | 48.1943 | 0.71517 | -0.2866 | 0.043262
CH_PLANT | The Centrepoint | 1/8/2024 7:00:00 pm | 88.8141 | 138.5828 | 159.4928 | 0.90082 | 83.5189 | -0.2866 | 0.043262
CH_PLANT | The Centrepoint | 1/8/2024 8:00:00 pm | 88.744 | 140.726 | 160.5523 | 0.0267 | 93.2616 | -0.2866 | 0.043262
CH_PLANT | The Centrepoint | 1/8/2024 9:00:00 pm | 88.6739 | 141.1152 | 159.5868 | 0.029 | 56.1047 | -0.067319 | 6.3709
CH_PLANT | The Centrepoint | 1/8/2024 10:00:00 pm | 88.6038 | 140.76 | 157.33 | 0.029 | 17.6902 | 0.034298 | 1553.082
CH_PLANT | The Centrepoint | 1/8/2024 11:00:00 pm | 88.5337 | 145.1577 | 158.5388 | 0.029 | 17.1311 | 0.034298 | 900.5404
CH_PLANT | The Centrepoint | 2/8/2024 12:00:00 am | 88.4636 | 141.3635 | 1.6907 | 0.029 | 10.3691 | 0.034298 | 0.32157
CH_PLANT | The Centrepoint | 2/8/2024 1:00:00 am | 88.3934 | 143.7097 | 1.25 | 0.029 | 12.119 | 0.023504 | 0.039287
CH_PLANT | The Centrepoint | 2/8/2024 2:00:00 am | 88.3233 | 143.32 | 1.25 | 0.029 | 9.429 | 0.13675 | 0.039036
CH_PLANT | The Centrepoint | 2/8/2024 3:00:00 am | 88.2532 | 139.692 | 1.25 | 0.029 | 8.9298 | -0.14278 | 0.038355
CH_PLANT | The Centrepoint | 2/8/2024 4:00:00 am | 88.1831 | 0.83 | 1.25 | 0.029 | 10.0366 | -0.13003 | 0.038355
CH_PLANT | The Centrepoint | 2/8/2024 5:00:00 am | 88.113 | 0.83 | 1.25 | 0.028833 | 7.0211 | -0.1194 | 0.034431
CH_PLANT | The Centrepoint | 2/8/2024 6:00:00 am | 88.0429 | 0.83 | 1.25 | 1.2127 | 9.1607 | 0.081239 | 0.027654
CH_PLANT | The Centrepoint | 2/8/2024 7:00:00 am | 87.9728 | 0.83 | 142.9307 | 70.9289 | 0.73104 | -0.2202 | 0.037175
CH_PLANT | The Centrepoint | 2/8/2024 8:00:00 am | 87.9027 | 0.83 | 283.9762 | 42.8245 | 0.70969 | -0.33499 | 0.037677
CH_PLANT | The Centrepoint | 2/8/2024 9:00:00 am | 87.8326 | 0.83 | 155.5683 | 40.9779 | 0.67503 | -0.33499 | 0.037677
CH_PLANT | The Centrepoint | 2/8/2024 10:00:00 am | 87.7625 | 0.83 | 159.8705 | 40.9816 | 0.65245 | 135.4711 | 0.035654
CH_PLANT | The Centrepoint | 2/8/2024 11:00:00 am | 87.6923 | 0.83 | 159.8542 | 41.0895 | 0.63801 | 135.4711 | 5.7509
CH_PLANT | The Centrepoint | 2/8/2024 12:00:00 pm | 87.6222 | 0.83 | 160.6118 | 41.0359 | 0.64496 | 135.4711 | 1944.854
CH_PLANT | The Centrepoint | 2/8/2024 1:00:00 pm | 87.5521 | 0.83 | 163.082 | 41.1324 | 0.64728 | 135.4711 | 983.0244
CH_PLANT | The Centrepoint | 2/8/2024 2:00:00 pm | 87.482 | 0.83 | 159.8013 | 41.0387 | 0.64627 | 135.4711 | 0.32158
CH_PLANT | The Centrepoint | 2/8/2024 3:00:00 pm | 87.4119 | 0.83 | 161.696 | 41.1871 | 0.64315 | 135.4711 | 0.05447
CH_PLANT | The Centrepoint | 2/8/2024 4:00:00 pm | 87.3418 | 222.2117 | 161.149 | 41.0378 | 0.62559 | 65.4282 | 0.062073
CH_PLANT | The Centrepoint | 2/8/2024 5:00:00 pm | 87.2717 | 121.7788 | 158.0473 | 41.1095 | 0.63305 | -0.15394 | 0.052725
CH_PLANT | The Centrepoint | 2/8/2024 6:00:00 pm | 87.2016 | 140.3862 | 159.2922 | 41.106 | 0.63221 | -0.14521 | 0.050175
CH_PLANT | The Centrepoint | 2/8/2024 6:00:00 pm | 87.1315 | 141.6088 | 157.01 | 40.9408 | 0.78051 | 1.1826 | 0.050175
CH_PLANT | The Centrepoint | 2/8/2024 7:00:00 pm | 87.0614 | 142.576 | 158.9154 | 0.95423 | 6.18 | -0.18117 | 862.9459
CH_PLANT | The Centrepoint | 2/8/2024 8:00:00 pm | 86.9913 | 142.2313 | 1.803 | 0.023 | 6.18 | -0.49755 | 896.6569
CH_PLANT | The Centrepoint | 2/8/2024 9:00:00 pm | 86.9211 | 142.9318 | 0.83 | 0.023 | 33.9825 | 1.3084 | 1038.853
CH_PLANT | The Centrepoint | 2/8/2024 10:00:00 pm | 86.851 | 143.4013 | 0.83 | 0.023 | 26.6293 | 4.3057 | 1048.434
CH_PLANT | The Centrepoint | 2/8/2024 11:00:00 pm | 86.7809 | 143.1827 | 0.83 | 0.023 | 19.0397 | 7.5565 | 1038.186
CH_PLANT | The Centrepoint | 3/8/2024 12:00:00 am | 86.7108 | 141.9587 | 0.83 | 0.023 | 11.2898 | 9.063 | 1040.852
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.6407 | 139.8857 | 0.83 | 0.028 | 8.9551 | 9.6894 | 1058.503
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 1:00:00 am | 86.5706 | 141.27 | 0.83 | 0.028 | 6.7642 | 12.821 | 1024.989
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 2:00:00 am | 86.5005 | 141.7941 | 0.83 | 0.028 | 8.3708 | 15.5577 | 1065.603
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 am | 86.4304 | 211.3907 | 0.83 | 0.028 | 8.4711 | 15.6908 | 1068.949
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 4:00:00 am | 86.3603 | 125.0453 | 0.83 | 0.028 | 7.1738 | 25.7542 | 1064.135
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 5:00:00 am | 86.2902 | 122.1157 | 0.83 | 0.028 | 10.6001 | -0.098259 | 870.7095
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 6:00:00 am | 86.22 | 134.7627 | 1.821 | 36.8521 | 4.5268 | -0.14402 | 900.9366
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 7:00:00 am | 86.1499 | 142.0195 | 350.1997 | 70.7896 | 0.76155 | 0.33319 | 907.2243
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 8:00:00 am | 86.0798 | 141.0818 | 281.2738 | 42.8775 | 0.68755 | -0.083678 | 893.1748
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 9:00:00 am | 86.0097 | 144.3085 | 175.87 | 41.1297 | 0.62809 | -0.099753 | 1039.508
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 10:00:00 am | 85.9396 | 143.05 | 160.6298 | 40.9786 | 0.6242 | 0.76645 | 1030.996
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 11:00:00 am | 85.8695 | 144.1205 | 157.7287 | 41.0366 | 0.62774 | 6.3262 | 1043.581
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 12:00:00 pm | 85.7994 | 144.5835 | 159.88 | 41.0893 | 0.63871 | 6.7394 | 1031.573
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 1:00:00 pm | 85.7293 | 265.318 | 160.2983 | 40.996 | 0.63407 | 12.6395 | 1058.812
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 2:00:00 pm | 85.6592 | 247.75 | 160.0222 | 40.9035 | 0.64034 | 18.9155 | 1063.401
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.5891 | 127.7817 | 164.0948 | 41.1374 | 0.62836 | 20.4281 | 1057.548
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 4:00:00 pm | 85.519 | 280.6798 | 160.5053 | 40.9563 | 0.6121 | 21.0207 | 871.9294
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 5:00:00 pm | 85.4488 | 235.2458 | 162.7955 | 41.0798 | 0.62325 | 28.5815 | 943.1224
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 6:00:00 pm | 85.3787 | 168.3037 | 162.3 | 41.331 | 0.63779 | 21.9881 | 1033.666
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 6:00:00 pm | 85.3086 | 145.1907 | 158.752 | 40.771 | 0.69522 | 0.029592 | 1056.056
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 7:00:00 pm | 85.2385 | 142.3572 | 1.8103 | 0.78508 | 2.3258 | -0.15671 | 1061.255
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 8:00:00 pm | 85.1684 | 143.2948 | 0.83 | 0.027 | 2.3258 | -0.10205 | 1041.611
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 9:00:00 pm | 85.0983 | 143.8213 | 0.83 | 0.027 | 60.3223 | -0.61256 | 1036.183
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 10:00:00 pm | 85.0282 | 143.0695 | 0.83 | 0.027 | 28.2539 | -0.65419 | 1048.572
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 11:00:00 pm | 84.9581 | 143.0172 | 0.83 | 0.027 | 11.6679 | -0.56783 | 1050.892
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 12:00:00 am | 84.888 | 144.2282 | 0.83 | 0.027 | 10.9317 | 1.5811 | 1067.901
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 1:00:00 am | 84.8179 | 142.4952 | 0.83 | 0.027 | 9.8918 | 2.781 | 1066.451
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 2:00:00 am | 84.7478 | 146.19 | 0.83 | 0.025433 | 7.504 | 4.1667 | 1164.098
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 3:00:00 am | 84.6776 | 137.2217 | 0.83 | 0.025 | 9.4065 | 7.3829 | 1024.813
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 4:00:00 am | 84.6075 | 0.83 | 0.83 | 0.025 | 6.7286 | 9.0097 | 1033.186
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 5:00:00 am | 84.5374 | 0.83 | 0.83 | 0.025 | 7.1923 | 12.269 | 1037.898
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 6:00:00 am | 84.4673 | 0.83 | 1.566 | 1.2336 | 8.6973 | 13.1164 | 1048.092
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 7:00:00 am | 84.3972 | 0.83 | 257.5662 | 72.6787 | 0.91059 | 20.5579 | 1025.973
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 8:00:00 am | 84.3271 | 0.83 | 141.2028 | 72.349 | 0.73698 | -0.068321 | 1036.719
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 9:00:00 am | 84.257 | 0.83 | 159.5533 | 48.2704 | 0.71584 | -0.096173 | 1041.856
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 10:00:00 am | 84.1869 | 0.82 | 160.7277 | 40.9349 | 0.64356 | 1.2825 | 1046.74
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 11:00:00 am | 84.1168 | 0.82 | 161.6722 | 40.8956 | 0.64135 | -0.0037894 | 1051.684
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 12:00:00 pm | 84.0467 | 0.82 | 161.3202 | 40.8453 | 0.63981 | -0.059149 | 1006.404
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 1:00:00 pm | 83.9765 | 0.82 | 162.0658 | 40.8835 | 0.64295 | 2.6875 | 985.1463
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 2:00:00 pm | 83.9064 | 0.82 | 162.4497 | 40.993 | 0.63405 | 4.0545 | 1051.923
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 3:00:00 pm | 83.8363 | 0.82 | 162.3155 | 40.877 | 0.65094 | 4.5709 | 1026.88
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 4:00:00 pm | 83.7662 | 0.82 | 161.0215 | 40.8466 | 0.62832 | 9.3657 | 1033.496
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 5:00:00 pm | 83.6961 | 0.82 | 158.8972 | 41.0233 | 0.63474 | 10.2887 | 1031.245
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 6:00:00 pm | 83.626 | 0.82 | 160.46 | 40.302 | 0.65138 | 12.2243 | 1031.94
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 6:00:00 pm | 83.5559 | 0.82 | 160.8549 | 40.8383 | 1.5193 | 15.2955 | 1032.83
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 7:00:00 pm | 83.4858 | 0.82 | 1.8115 | 0.80522 | 50.4839 | 15.2891 | 1031.736
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 8:00:00 pm | 83.4157 | 0.82 | 0.83 | 0.029067 | 50.4839 | 15.1245 | 1047.3
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 9:00:00 pm | 83.3456 | 0.82 | 0.83 | 0.02285 | 58.4958 | -0.074615 | 1066.75
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 10:00:00 pm | 83.2755 | 0.82 | 0.83 | 0.023167 | 33.253 | -0.14985 | 1059.366
CH_PLANT | Tiong Bahru Plaza | 30/7/2024 11:00:00 pm | 83.2053 | 0.82 | 0.83 | 0.023 | 15.5205 | -0.33667 | 859.2554
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 12:00:00 am | 83.1352 | 0.82 | 0.83 | 0.023 | 11.1049 | -0.51807 | 924.161
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 1:00:00 am | 83.0651 | 0.82 | 0.83 | 0.023 | 11.9385 | -0.53118 | 908.1718
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 2:00:00 am | 82.995 | 0.82 | 0.83 | 0.023 | 8.348 | 0.85671 | 925.0761
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 3:00:00 am | 82.9249 | 0.82 | 0.83 | 0.023 | 10.1424 | 3.8126 | 992.4328
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 4:00:00 am | 82.8548 | 0.82 | 0.83 | 0.023 | 7.7654 | 4.9252 | 1029.748
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 5:00:00 am | 82.7847 | 0.82 | 0.83 | 0.023917 | 7.3475 | 519.5868 | 1046.874
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 6:00:00 am | 82.7146 | 0.82 | 1.606 | 1.2107 | 9.0175 | 519.5868 | 1027.061
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 7:00:00 am | 82.6445 | 0.82 | 247.0683 | 69.8127 | 0.70746 | 519.5868 | 1043.921
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 8:00:00 am | 82.5744 | 0.82 | 144.425 | 40.7521 | 0.66427 | 519.5868 | 1726.136
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 9:00:00 am | 82.5042 | 0.82 | 141.3698 | 40.903 | 0.63797 | 474.4282 | 1529.332
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 10:00:00 am | 82.4341 | 0.82 | 153.9807 | 40.8578 | 0.64983 | 335.3918 | 857.3879
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 11:00:00 am | 82.364 | 0.82 | 161.1778 | 40.837 | 0.64628 | 162.0615 | 972.3392
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 12:00:00 pm | 82.2939 | 0.82 | 160.195 | 40.8798 | 0.64557 | -0.16663 | 1018.362
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 1:00:00 pm | 82.2238 | 0.82 | 163.2928 | 40.927 | 0.65392 | -0.16247 | 1038.569
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 2:00:00 pm | 82.1537 | 0.82 | 162.1948 | 40.8882 | 0.65862 | 0.09563 | 1022.918
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 3:00:00 pm | 82.0836 | 0.82 | 163.2433 | 40.9517 | 0.65602 | -0.38016 | 1011.85
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 4:00:00 pm | 82.0135 | 0.82 | 164.0872 | 41.0271 | 0.63566 | -0.3892 | 1031.375
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 5:00:00 pm | 81.9434 | 0.82 | 297.1015 | 40.9806 | 0.63438 | 2.006 | 1020.958
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 6:00:00 pm | 81.8733 | 0.82 | 392.14 | 42.115 | 0.63067 | 4.7174 | 1044.704
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 6:00:00 pm | 81.8032 | 0.82 | 147.4105 | 40.8536 | 0.7504 | 10.5061 | 1039.928
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 7:00:00 pm | 81.733 | 0.82 | 1.6167 | 0.79662 | 4.3689 | 10.778 | 1039.508
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 8:00:00 pm | 81.6629 | 0.82 | 1.6783 | 0.029 | 4.3689 | 10.8413 | 917.033
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 9:00:00 pm | 81.5928 | 0.82 | 315.7033 | 0.029 | 27.4066 | 11.3776 | 1043.856
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 10:00:00 pm | 81.5227 | 0.82 | 269.4812 | 0.029 | 36.4171 | 12.0136 | 1068.608
CH_PLANT | Tiong Bahru Plaza | 31/7/2024 11:00:00 pm | 81.4526 | 0.82 | 194.1592 | 0.029 | 15.7932 | 12.0136 | 1062.827
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 12:00:00 am | 81.3825 | 0.82 | 164.454 | 0.029 | 12.5621 | 13.5211 | 1061.97
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 1:00:00 am | 81.3124 | 0.82 | 161.5215 | 0.029 | 12.1175 | -0.10711 | 1049.042
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 2:00:00 am | 81.2423 | 0.82 | 162.4512 | 0.029 | 8.293 | -0.16377 | 1058.536
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 3:00:00 am | 81.1722 | 0.82 | 163.0525 | 0.029 | 10.2453 | -0.26544 | 1069.365
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 4:00:00 am | 81.1021 | 0.82 | 162.2298 | 0.029 | 7.0494 | -0.65973 | 1080.882
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 5:00:00 am | 81.032 | 0.82 | 161.6363 | 0.029 | 7.4736 | -0.75466 | 1054.089
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 6:00:00 am | 80.9618 | 0.82 | 161.6212 | 1.2184 | 8.4863 | -0.22711 | 1033.741
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 7:00:00 am | 80.8917 | 0.82 | 159.6117 | 67.4144 | 0.70809 | 1.9337 | 1645.933
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 8:00:00 am | 80.8216 | 0.82 | 163.45 | 40.6611 | 0.67958 | 2.7027 | 1089.653
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 9:00:00 am | 80.7515 | 0.82 | 154.4307 | 40.472 | 0.67429 | 6.4673 | 1035.09
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 10:00:00 am | 80.6814 | 0.82 | 1.6485 | 40.7071 | 0.64985 | 7.6585 | 1037.43
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 11:00:00 am | 80.6113 | 0.82 | 0.83 | 40.8074 | 0.63741 | 9.1501 | 1046.247
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 12:00:00 pm | 80.5412 | 0.82 | 0.83 | 40.9122 | 0.63806 | 11.7132 | 1048.535
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 1:00:00 pm | 80.4711 | 0.82 | 0.83 | 40.9128 | 0.64486 | 16.0617 | 1057.161
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 2:00:00 pm | 80.401 | 0.82 | 0.83 | 40.9515 | 0.64904 | 19.4863 | 1053.772
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 3:00:00 pm | 80.3309 | 0.82 | 0.83 | 40.9115 | 0.65838 | -0.13261 | 1061.198
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 4:00:00 pm | 80.2607 | 0.82 | 0.82 | 44.5145 | 0.64225 | -0.15931 | 1067.24
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 5:00:00 pm | 80.1906 | 0.82 | 0.82 | 72.1615 | 0.75068 | -0.15236 | 1080.798
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 6:00:00 pm | 80.1205 | 0.82 | 0.82 | 71.379 | 1.2173 | -0.43905 | 864.3814
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 6:00:00 pm | 80.0504 | 0.82 | 0.82 | 44.9245 | 0.76314 | -0.47467 | 1024.406
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 7:00:00 pm | 79.9803 | 0.82 | 0.82 | 0.75627 | 4.453 | -0.24711 | 1039.213
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 8:00:00 pm | 79.9102 | 0.82 | 0.82 | 0.026 | 4.453 | 3.4996 | 1053.893
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 9:00:00 pm | 79.8401 | 0.82 | 0.82 | 0.026 | 4.453 | 4.627 | 1045.208
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 10:00:00 pm | 79.77 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.611
CH_PLANT | Tiong Bahru Plaza | 1/8/2024 11:00:00 pm | 79.6999 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1028.992
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 12:00:00 am | 79.6298 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.406
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 1:00:00 am | 79.5597 | 0.82 | 0.82 | 0.026 | 4.453 | 8.8144 | 1051.324
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 2:00:00 am | 79.4895 | 0.82 | 0.82 | 0.026 | 4.453 | 11.5816 | 1049.278
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 3:00:00 am | 79.4194 | 0.82 | 0.82 | 0.026 | 4.453 | 15.2228 | 1055.082
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 4:00:00 am | 79.3493 | 0.82 | 0.82 | 0.026 | 4.453 | -0.094059 | 877.9323
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 5:00:00 am | 79.2792 | 0.82 | 0.82 | 0.026 | 17.1926 | -0.12636 | 884.2773
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 6:00:00 am | 79.2091 | 0.82 | 0.82 | 1.2471 | 51.037 | -0.022934 | 970.1237
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 7:00:00 am | 79.139 | 0.82 | 0.82 | 72.5447 | 0.69187 | -0.2911 | 1061.106
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 8:00:00 am | 79.0689 | 0.82 | 0.82 | 72.2521 | 0.74228 | -0.33163 | 1058.15
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 9:00:00 am | 78.9988 | 0.82 | 0.82 | 53.7303 | 0.69685 | -0.32213 | 1056.86
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 10:00:00 am | 78.9287 | 0.82 | 0.82 | 40.9114 | 0.65995 | -0.32213 | 1040.489
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 11:00:00 am | 78.8586 | 0.82 | 0.82 | 40.9621 | 0.65312 | -0.22594 | 1033.822
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 12:00:00 pm | 78.7885 | 0.82 | 0.82 | 40.9006 | 0.65033 | -0.059809 | 1071.282
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 1:00:00 pm | 78.7183 | 0.82 | 0.82 | 40.934 | 0.65789 | -0.29741 | 1727.56
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 2:00:00 pm | 78.6482 | 0.82 | 0.82 | 40.9187 | 0.65846 | -0.30991 | 1539.706
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 3:00:00 pm | 78.5781 | 0.82 | 0.82 | 40.9878 | 0.65259 | -0.30991 | 1561.595
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 4:00:00 pm | 78.508 | 0.82 | 0.82 | 40.8562 | 0.64558 | -0.25927 | 1158.264
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 5:00:00 pm | 78.4379 | 0.82 | 0.82 | 40.9364 | 0.64336 | 0.72283 | 1033.918
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 6:00:00 pm | 78.3678 | 0.82 | 0.82 | 40.757 | 0.66113 | -0.040134 | 1032.46
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 6:00:00 pm | 78.2977 | 0.82 | 0.82 | 40.7378 | 0.70649 | -0.16181 | 1046.441
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 7:00:00 pm | 78.2276 | 0.82 | 0.82 | 0.79742 | 1.9423 | -0.22997 | 1036.824
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 8:00:00 pm | 78.1575 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48001 | 1024.879
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 9:00:00 pm | 78.0874 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.56223 | 1042.816
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 10:00:00 pm | 78.0172 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48538 | 1045.783
CH_PLANT | Tiong Bahru Plaza | 2/8/2024 11:00:00 pm | 77.9471 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1039.836
CH_PLANT | Tiong Bahru Plaza | 3/8/2024 12:00:00 am | 77.877 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1043.321
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.8069 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 1:00:00 am | 77.7368 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 2:00:00 am | 77.6667 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 am | 77.5966 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 4:00:00 am | 77.5265 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | Causeway Point | 29/7/2024 5:00:00 am | 77.4564 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | Causeway Point | 29/7/2024 6:00:00 am | 77.3863 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | Causeway Point | 29/7/2024 7:00:00 am | 77.3162 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | Causeway Point | 29/7/2024 8:00:00 am | 77.246 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | Causeway Point | 29/7/2024 9:00:00 am | 77.1759 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | Causeway Point | 29/7/2024 10:00:00 am | 77.1058 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | Causeway Point | 29/7/2024 11:00:00 am | 77.0357 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | Causeway Point | 29/7/2024 12:00:00 pm | 76.9656 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | Causeway Point | 29/7/2024 1:00:00 pm | 76.8955 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | Causeway Point | 29/7/2024 2:00:00 pm | 76.8254 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.7553 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | Causeway Point | 29/7/2024 4:00:00 pm | 76.6852 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | Causeway Point | 29/7/2024 5:00:00 pm | 76.6151 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | Causeway Point | 29/7/2024 6:00:00 pm | 76.5449 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | Causeway Point | 29/7/2024 6:00:00 pm | 76.4748 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | Causeway Point | 29/7/2024 7:00:00 pm | 76.4047 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | Causeway Point | 29/7/2024 8:00:00 pm | 76.3346 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | Causeway Point | 29/7/2024 9:00:00 pm | 76.2645 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | Causeway Point | 29/7/2024 10:00:00 pm | 76.1944 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | Causeway Point | 29/7/2024 11:00:00 pm | 76.1243 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | Causeway Point | 30/7/2024 12:00:00 am | 76.0542 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 30/7/2024 1:00:00 am | 75.9841 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | Causeway Point | 30/7/2024 2:00:00 am | 75.914 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 30/7/2024 3:00:00 am | 75.8439 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 30/7/2024 4:00:00 am | 75.7737 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 30/7/2024 5:00:00 am | 75.7036 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | Causeway Point | 30/7/2024 6:00:00 am | 75.6335 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | Causeway Point | 30/7/2024 7:00:00 am | 75.5634 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | Causeway Point | 30/7/2024 8:00:00 am | 75.4933 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | Causeway Point | 30/7/2024 9:00:00 am | 75.4232 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | Causeway Point | 30/7/2024 10:00:00 am | 75.3531 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | Causeway Point | 30/7/2024 11:00:00 am | 75.283 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | Causeway Point | 30/7/2024 12:00:00 pm | 75.2129 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | Causeway Point | 30/7/2024 1:00:00 pm | 75.1428 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | Causeway Point | 30/7/2024 2:00:00 pm | 75.0727 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | Causeway Point | 30/7/2024 3:00:00 pm | 75.0025 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | Causeway Point | 30/7/2024 4:00:00 pm | 74.9324 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | Causeway Point | 30/7/2024 5:00:00 pm | 74.8623 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | Causeway Point | 30/7/2024 6:00:00 pm | 74.7922 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | Causeway Point | 30/7/2024 6:00:00 pm | 74.7221 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | Causeway Point | 30/7/2024 7:00:00 pm | 74.652 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | Causeway Point | 30/7/2024 8:00:00 pm | 74.5819 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | Causeway Point | 30/7/2024 9:00:00 pm | 74.5118 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | Causeway Point | 30/7/2024 10:00:00 pm | 74.4417 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | Causeway Point | 30/7/2024 11:00:00 pm | 74.3716 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | Causeway Point | 31/7/2024 12:00:00 am | 74.3014 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 31/7/2024 1:00:00 am | 74.2313 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 31/7/2024 2:00:00 am | 74.1612 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 31/7/2024 3:00:00 am | 74.0911 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 31/7/2024 4:00:00 am | 74.021 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 31/7/2024 5:00:00 am | 73.9509 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 31/7/2024 6:00:00 am | 73.8808 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | Causeway Point | 31/7/2024 7:00:00 am | 73.8107 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | Causeway Point | 31/7/2024 8:00:00 am | 73.7406 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | Causeway Point | 31/7/2024 9:00:00 am | 73.6705 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | Causeway Point | 31/7/2024 10:00:00 am | 73.6004 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | Causeway Point | 31/7/2024 11:00:00 am | 73.5302 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | Causeway Point | 31/7/2024 12:00:00 pm | 73.4601 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | Causeway Point | 31/7/2024 1:00:00 pm | 73.39 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | Causeway Point | 31/7/2024 2:00:00 pm | 73.3199 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | Causeway Point | 31/7/2024 3:00:00 pm | 73.2498 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | Causeway Point | 31/7/2024 4:00:00 pm | 73.1797 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | Causeway Point | 31/7/2024 5:00:00 pm | 73.1096 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | Causeway Point | 31/7/2024 6:00:00 pm | 73.0395 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | Causeway Point | 31/7/2024 6:00:00 pm | 72.9694 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | Causeway Point | 31/7/2024 7:00:00 pm | 72.8993 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | Causeway Point | 31/7/2024 8:00:00 pm | 72.8291 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | Causeway Point | 31/7/2024 9:00:00 pm | 72.759 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | Causeway Point | 31/7/2024 10:00:00 pm | 72.6889 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 31/7/2024 11:00:00 pm | 72.6188 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 1/8/2024 12:00:00 am | 72.5487 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | Causeway Point | 1/8/2024 1:00:00 am | 72.4786 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | Causeway Point | 1/8/2024 2:00:00 am | 72.4085 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | Causeway Point | 1/8/2024 3:00:00 am | 72.3384 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | Causeway Point | 1/8/2024 4:00:00 am | 72.2683 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | Causeway Point | 1/8/2024 5:00:00 am | 72.1982 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | Causeway Point | 1/8/2024 6:00:00 am | 72.1281 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | Causeway Point | 1/8/2024 7:00:00 am | 72.0579 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | Causeway Point | 1/8/2024 8:00:00 am | 71.9878 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | Causeway Point | 1/8/2024 9:00:00 am | 71.9177 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | Causeway Point | 1/8/2024 10:00:00 am | 71.8476 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | Causeway Point | 1/8/2024 11:00:00 am | 71.7775 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | Causeway Point | 1/8/2024 12:00:00 pm | 71.7074 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | Causeway Point | 1/8/2024 1:00:00 pm | 71.6373 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | Causeway Point | 1/8/2024 2:00:00 pm | 71.5672 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | Causeway Point | 1/8/2024 3:00:00 pm | 71.4971 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | Causeway Point | 1/8/2024 4:00:00 pm | 71.427 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | Causeway Point | 1/8/2024 5:00:00 pm | 71.3569 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | Causeway Point | 1/8/2024 6:00:00 pm | 71.2867 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | Causeway Point | 1/8/2024 6:00:00 pm | 71.2166 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | Causeway Point | 1/8/2024 7:00:00 pm | 71.1465 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | Causeway Point | 1/8/2024 8:00:00 pm | 71.0764 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | Causeway Point | 1/8/2024 9:00:00 pm | 71.0063 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | Causeway Point | 1/8/2024 10:00:00 pm | 70.9362 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | Causeway Point | 1/8/2024 11:00:00 pm | 70.8661 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | Causeway Point | 2/8/2024 12:00:00 am | 70.796 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | Causeway Point | 2/8/2024 1:00:00 am | 70.7259 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | Causeway Point | 2/8/2024 2:00:00 am | 70.6558 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | Causeway Point | 2/8/2024 3:00:00 am | 70.5856 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | Causeway Point | 2/8/2024 4:00:00 am | 70.5155 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | Causeway Point | 2/8/2024 5:00:00 am | 70.4454 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | Causeway Point | 2/8/2024 6:00:00 am | 70.3753 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | Causeway Point | 2/8/2024 7:00:00 am | 70.3052 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | Causeway Point | 2/8/2024 8:00:00 am | 70.2351 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | Causeway Point | 2/8/2024 9:00:00 am | 70.165 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | Causeway Point | 2/8/2024 10:00:00 am | 70.0949 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | Causeway Point | 2/8/2024 11:00:00 am | 70.0248 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | Causeway Point | 2/8/2024 12:00:00 pm | 69.9547 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | Causeway Point | 2/8/2024 1:00:00 pm | 69.8846 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | Causeway Point | 2/8/2024 2:00:00 pm | 69.8144 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | Causeway Point | 2/8/2024 3:00:00 pm | 69.7443 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766
CH_PLANT | Causeway Point | 2/8/2024 4:00:00 pm | 69.6742 | 131.7272 | 159.2118 | 41.079 | 0.62344 | -0.10051 | 0.040715
CH_PLANT | Causeway Point | 2/8/2024 5:00:00 pm | 69.6041 | 139.838 | 159.4572 | 40.9576 | 0.63158 | -0.10622 | 0.037693
CH_PLANT | Causeway Point | 2/8/2024 6:00:00 pm | 69.534 | 142.3787 | 156.58 | 40.127 | 0.65917 | -0.059145 | 0.037693
CH_PLANT | Causeway Point | 2/8/2024 6:00:00 pm | 69.4639 | 142.9808 | 159.9854 | 40.9299 | 0.67922 | -0.084936 | 0.037693
CH_PLANT | Causeway Point | 2/8/2024 7:00:00 pm | 69.3938 | 141.9497 | 150.8555 | 40.908 | 0.69374 | -0.10325 | 0.035985
CH_PLANT | Causeway Point | 2/8/2024 8:00:00 pm | 69.3237 | 142.9197 | 138.1777 | 40.916 | 0.69775 | -0.10198 | 0.027444
CH_PLANT | Causeway Point | 2/8/2024 9:00:00 pm | 69.2536 | 141.6483 | 6.752 | 3.4926 | 83.086 | -0.10838 | 0.027444
CH_PLANT | Causeway Point | 2/8/2024 10:00:00 pm | 69.1835 | 137.604 | 0.84 | 0.027 | 100 | -0.11046 | 0.027444
CH_PLANT | Causeway Point | 2/8/2024 11:00:00 pm | 69.1134 | 140.7528 | 0.84 | 0.027 | 100 | -0.10784 | 5.3268
CH_PLANT | Causeway Point | 3/8/2024 12:00:00 am | 69.0432 | 136.84 | 0.84 | 0.027 | 100 | -0.11336 | 1989.365
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.15264 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.15264 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.15264 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.15264 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.15264 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.15264 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 230.1518 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 353.595 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 232.9173 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 258.2021 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 258.2727 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 259.1299 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 258.5767 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 374.6179 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 356.8681 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 353.213 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 367.8326 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 364.8911 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 322.467 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 219.8944 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 156.8479 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 209.2716 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 10.5742 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.007655 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 8.3935 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 383.8692 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 229.3992 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 253.1832 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 253.8745 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 309.7934 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 353.5703 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 247.2451 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 250.1999 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 249.9489 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 252.2253 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 259.2637 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 255.7154 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 237.3407 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 230.4723 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 214.3843 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 8.1023 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 7.2616 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 382.2976 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 214.4432 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 230.3184 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 250.4467 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 253.9743 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 251.2279 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 250.5016 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 252.5164 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 255.5416 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 257.9506 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 257.7903 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 247.8403 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 240.8013 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 219.9641 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 200.6285 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 10.0851 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 7.4451 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 341.0601 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 208.3729 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 216.7669 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 252.1507 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 251.3926 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 248.3258 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 250.021 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 252.2408 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 246.6578 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 256.239 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 259.0186 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 240.1991 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 246.6867 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 222.663 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 200.1667 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 10.4129 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0.9848 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 346.465 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 209.1722 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 214.7381 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 216.052 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 214.4598 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 252.7742 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 248.0521 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 249.4566 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 246.539 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 255.1459 | 131.7272 | 159.2118 | 41.079 | 0.62344 | -0.10051 | 0.040715
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 252.438 | 139.838 | 159.4572 | 40.9576 | 0.63158 | -0.10622 | 0.037693
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 235.5223 | 142.3787 | 156.58 | 40.127 | 0.65917 | -0.059145 | 0.037693
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 240.9999 | 142.9808 | 159.9854 | 40.9299 | 0.67922 | -0.084936 | 0.037693
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 217.6346 | 141.9497 | 150.8555 | 40.908 | 0.69374 | -0.10325 | 0.035985
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 197.8981 | 142.9197 | 138.1777 | 40.916 | 0.69775 | -0.10198 | 0.027444
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 7.8362 | 141.6483 | 6.752 | 3.4926 | 83.086 | -0.10838 | 0.027444
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 137.604 | 0.84 | 0.027 | 100 | -0.11046 | 0.027444
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 140.7528 | 0.84 | 0.027 | 100 | -0.10784 | 5.3268
CH_PLANT | North Point City (North Wing) | 29/7/2024 3:00:00 pm | 0 | 136.84 | 0.84 | 0.027 | 100 | -0.11336 | 1989.365
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1556 | 141.4985 | 1.23 | 0.024 | 6.6646 | -0.11491 | 1021.944
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1556 | 0.83 | 1.23 | 0.024 | 7.3577 | -0.10588 | 0.549
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1556 | 0.83 | 1.23 | 0.024 | 5.7515 | -0.11082 | 0.032093
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1556 | 0.83 | 1.23 | 0.024 | 7.6403 | -0.13482 | 0.033581
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1556 | 0.83 | 1.23 | 0.024 | 6.4198 | -0.08407 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1556 | 0.83 | 1.23 | 0.024 | 5.6763 | -0.11678 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 228.7117 | 0.83 | 145.6395 | 36.886 | 4.3894 | -0.11124 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 355.3201 | 0.83 | 263.8778 | 70.8171 | 0.74909 | -0.11493 | 0.028869
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 213.9598 | 0.83 | 143.6267 | 42.9785 | 0.68202 | -0.09018 | 0.020435
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 227.4719 | 0.83 | 150.3923 | 40.7452 | 0.66066 | -0.10321 | 0.018327
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 256.7935 | 0.83 | 157.531 | 40.9629 | 0.61277 | -0.11586 | 0.018327
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 258.2658 | 0.83 | 159.9617 | 40.9678 | 0.61821 | -0.10567 | 0.018327
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 257.7781 | 0.83 | 160.407 | 41.0693 | 0.6237 | -0.093901 | 2.9502
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 255.4046 | 280.394 | 159.2295 | 41.0961 | 0.62318 | -0.14155 | 1566.063
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 251.9179 | 170.7897 | 160.1795 | 41.1538 | 0.63567 | -0.20497 | 1005.043
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 253.6264 | 142.1868 | 158.8533 | 41.0918 | 0.62736 | -0.077332 | 0.57226
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 255.6177 | 140.9953 | 154.8203 | 41.0734 | 0.60607 | -0.093229 | 0.061741
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 259.834 | 141.3117 | 158.0203 | 41.1464 | 0.60867 | -0.10299 | 0.074108
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 240.9619 | 142.0145 | 153.75 | 40.447 | 0.62025 | -0.10932 | 0.06796
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 251.8262 | 142.7058 | 158.8163 | 40.9356 | 0.65941 | -0.093705 | 0.061262
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 139.9993 | 1.7892 | 1.4081 | 15.9491 | -0.092 | 0.056499
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 139.8698 | 1.46 | 0.024 | 15.9491 | -0.10716 | 0.048864
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 140.4943 | 314.0868 | 0.024 | 33.2896 | -0.10601 | 0.046605
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.018348 | 138.0458 | 192.8402 | 0.024 | 25.2073 | -0.097927 | 0.038783
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.050039 | 135.91 | 159.6322 | 0.024 | 16.7405 | -0.10611 | 0.029609
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.08488 | 142.3993 | 158.3218 | 0.024 | 9.9003 | -0.13031 | 0.027377
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10103 | 221.4172 | 158.681 | 0.024 | 12.0921 | -0.076295 | 7.2576
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10103 | 137.7345 | 159.248 | 0.024 | 8.3197 | -0.10132 | 1667.161
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10103 | 144.3753 | 159.9183 | 0.024 | 7.8482 | -0.11949 | 961.0121
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.12238 | 143.3145 | 157.141 | 0.024 | 8.5625 | -0.11649 | 0.26549
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.12342 | 142.7942 | 157.0072 | 0.024 | 6.1329 | -0.11532 | 0.048098
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 2.1066 | 142.8697 | 157.6587 | 1.2388 | 7.6569 | -0.11547 | 0.052442
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 466.5208 | 143.6523 | 155.0962 | 72.8287 | 0.67636 | -0.12133 | 0.052442
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 281.7451 | 144.2565 | 153.18 | 50.2432 | 0.67834 | -0.11666 | 0.046237
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.7421 | 143.0503 | 159.5095 | 41.0497 | 0.63689 | -0.11995 | 0.041877
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 252.4842 | 141.0682 | 1.8083 | 41.0843 | 0.62837 | -0.10615 | 0.037509
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 252.6122 | 144.078 | 0.84 | 41.1265 | 0.62826 | -0.11515 | 0.037509
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 253.672 | 145.99 | 0.84 | 40.9531 | 0.6288 | -0.13933 | 0.033416
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.5889 | 140.0364 | 0.84 | 41.0044 | 0.6375 | -0.096132 | 0.026347
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.9931 | 1.2 | 0.84 | 41.0585 | 0.6279 | -0.11237 | 0.026347
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 252.1361 | 1.2 | 0.84 | 41.0366 | 0.62291 | -0.11498 | 3.4504
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 256.1362 | 1.2 | 0.84 | 40.9098 | 0.61563 | -0.12037 | 1666.068
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 255.5206 | 1.2 | 0.84 | 41.0441 | 0.60789 | -0.12485 | 1008.752
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 237.5489 | 1.2 | 0.84 | 42.061 | 0.58872 | -0.12308 | 0.41415
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 257.2703 | 1.2 | 0.84 | 40.914 | 0.68759 | -0.11821 | 0.049389
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 1.2 | 0.84 | 1.4067 | 21.9641 | -0.11876 | 0.049699
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 1.2 | 1.2152 | 0.027117 | 21.9641 | -0.1167 | 0.044414
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 1.2 | 250.7245 | 0.029483 | 34.4065 | -0.16476 | 0.042329
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.006012 | 1.2 | 157.5758 | 0.02985 | 26.4288 | -0.086652 | 0.033989
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.051535 | 1.2 | 161.7642 | 0.03025 | 20.06 | -0.10189 | 0.001006
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.054998 | 1.2 | 160.5303 | 0.03 | 10.5145 | -0.12355 | 0.001006
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10348 | 240.5975 | 159.9868 | 0.029833 | 10.3076 | -0.12614 | 0.001006
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10348 | 124.592 | 159.9677 | 0.029833 | 9.8666 | -0.12018 | 0.001006
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10348 | 136.7727 | 160.8637 | 0.028783 | 7.3602 | -0.11768 | 0.001006
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10603 | 131.7778 | 161.479 | 0.030667 | 9.7727 | -0.11644 | 0.001006
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.14557 | 136.76 | 160.0555 | 0.030167 | 6.3896 | -0.11919 | 1009.799
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 1.0335 | 140.0172 | 158.195 | 0.69977 | 7.0595 | -0.11297 | 1671.116
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 365.0632 | 143.072 | 161.273 | 61.9782 | 0.66109 | -0.11959 | 1036.345
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 241.2598 | 142.5625 | 162.53 | 45.4487 | 0.65936 | -0.10959 | 0.24878
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 256.4374 | 142.6107 | 157.0676 | 41.1473 | 0.63108 | -0.10163 | 0.045289
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.4759 | 145.348 | 2.1613 | 41.0763 | 0.64021 | -0.1187 | 0.044205
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.2886 | 265.565 | 1.23 | 41.0747 | 0.63828 | -0.097798 | 0.044205
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 249.0823 | 239.71 | 1.23 | 41.1149 | 0.64312 | -0.12404 | 0.037228
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.0226 | 143.6597 | 1.23 | 41.0748 | 0.64221 | -0.12684 | 0.032892
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 248.6463 | 244.3348 | 1.23 | 41.0344 | 0.64824 | -0.11608 | 0.032892
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 247.9583 | 128.6923 | 1.23 | 41.0037 | 0.6462 | -0.11577 | 0.032892
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 254.4522 | 141.4727 | 1.23 | 41.1388 | 0.621 | -0.11551 | 0.032892
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 257.9779 | 142.4573 | 1.23 | 41.1382 | 0.62535 | -0.10978 | 0.032892
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 230.4184 | 140.9642 | 1.23 | 40.495 | 0.63516 | -0.14848 | 0.032892
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 249.0892 | 143.3018 | 1.23 | 40.8738 | 0.73453 | -0.21519 | 5.9819
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 141.8913 | 1.23 | 1.2019 | 38.2672 | -0.13602 | 2016.554
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 142.2788 | 1.9288 | 0.022833 | 38.2672 | -0.10063 | 1028.995
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 140.1968 | 276.5095 | 0.025517 | 38.2672 | -0.11335 | 0.46443
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 141.3907 | 145.4742 | 0.02915 | 47.7725 | -0.11737 | 0.087425
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.035571 | 140.492 | 156.0923 | 0.029017 | 25.0666 | -0.12104 | 0.093489
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.052055 | 139.35 | 151.097 | 0.028836 | 12.7812 | -0.1182 | 0.082881
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.064883 | 141.1839 | 155.9507 | 0.024383 | 11.9719 | -0.11327 | 0.071217
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10337 | 121.194 | 159.256 | 0.023433 | 11.6415 | -0.12573 | 0.062294
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10337 | 248.875 | 162.1848 | 0.024667 | 8.6229 | -0.1179 | 0.051746
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10337 | 134.2565 | 160.167 | 0.022583 | 12.1001 | -0.11933 | 0.045209
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.10337 | 140.4328 | 159.955 | 0.0215 | 8.3245 | -0.13251 | 0.038586
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 2.8605 | 140.6595 | 163.0452 | 1.192 | 9.7423 | -0.55642 | 0.030394
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 382.921 | 141.4652 | 298.5412 | 71.062 | 0.71877 | -0.48945 | 0.024451
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 210.5681 | 143.8553 | 271.85 | 42.7672 | 0.70324 | -0.32384 | 9.7405
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 220.4561 | 140.671 | 164.7647 | 40.6946 | 0.70861 | -0.18545 | 1621.899
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 217.8993 | 142.5722 | 1.6623 | 40.6721 | 0.69414 | 0.20734 | 1012.545
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 221.179 | 142.0108 | 1.4982 | 40.6807 | 0.70578 | 0.58086 | 0.48901
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 244.9366 | 138.9657 | 278.581 | 41.0242 | 0.65144 | 1.3976 | 0.052207
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.8755 | 140.1183 | 149.3538 | 41.0311 | 0.64721 | 0.013006 | 0.055203
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 251.4543 | 137.84 | 160.7307 | 41.0917 | 0.63682 | -0.14062 | 0.054199
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 249.4768 | 139.6983 | 161.7633 | 41.0286 | 0.63863 | -0.14404 | 0.045992
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 255.8599 | 283.4212 | 160.2337 | 44.2278 | 0.63777 | -0.1109 | 0.043262
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 399.1808 | 246.3632 | 162.5527 | 72.3453 | 0.74366 | 0.081825 | 0.043262
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 231.4076 | 152.9748 | 161.0952 | 71.715 | 0.83632 | -0.11574 | 0.043262
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 325.3193 | 141.4663 | 161.5225 | 48.1943 | 0.71517 | -0.2866 | 0.043262
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.26734 | 138.5828 | 159.4928 | 0.90082 | 83.5189 | -0.2866 | 0.043262
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.005783 | 140.726 | 160.5523 | 0.0267 | 93.2616 | -0.2866 | 0.043262
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.005783 | 141.1152 | 159.5868 | 0.029 | 56.1047 | -0.067319 | 6.3709
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.046738 | 140.76 | 157.33 | 0.029 | 17.6902 | 0.034298 | 1553.082
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.056977 | 145.1577 | 158.5388 | 0.029 | 17.1311 | 0.034298 | 900.5404
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.056977 | 141.3635 | 1.6907 | 0.029 | 10.3691 | 0.034298 | 0.32157
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.1023 | 143.7097 | 1.25 | 0.029 | 12.119 | 0.023504 | 0.039287
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.11215 | 143.32 | 1.25 | 0.029 | 9.429 | 0.13675 | 0.039036
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.11383 | 139.692 | 1.25 | 0.029 | 8.9298 | -0.14278 | 0.038355
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.11383 | 0.83 | 1.25 | 0.029 | 10.0366 | -0.13003 | 0.038355
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.11383 | 0.83 | 1.25 | 0.028833 | 7.0211 | -0.1194 | 0.034431
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 5.6557 | 0.83 | 1.25 | 1.2127 | 9.1607 | 0.081239 | 0.027654
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 381.8505 | 0.83 | 142.9307 | 70.9289 | 0.73104 | -0.2202 | 0.037175
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 211.26 | 0.83 | 283.9762 | 42.8245 | 0.70969 | -0.33499 | 0.037677
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 239.029 | 0.83 | 155.5683 | 40.9779 | 0.67503 | -0.33499 | 0.037677
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 248.0222 | 0.83 | 159.8705 | 40.9816 | 0.65245 | 135.4711 | 0.035654
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 251.2529 | 0.83 | 159.8542 | 41.0895 | 0.63801 | 135.4711 | 5.7509
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 251.8395 | 0.83 | 160.6118 | 41.0359 | 0.64496 | 135.4711 | 1944.854
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 249.4117 | 0.83 | 163.082 | 41.1324 | 0.64728 | 135.4711 | 983.0244
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 250.1121 | 0.83 | 159.8013 | 41.0387 | 0.64627 | 135.4711 | 0.32158
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 247.7325 | 0.83 | 161.696 | 41.1871 | 0.64315 | 135.4711 | 0.05447
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 256.2571 | 222.2117 | 161.149 | 41.0378 | 0.62559 | 65.4282 | 0.062073
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 252.5853 | 121.7788 | 158.0473 | 41.1095 | 0.63305 | -0.15394 | 0.052725
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 233.4623 | 140.3862 | 159.2922 | 41.106 | 0.63221 | -0.14521 | 0.050175
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 245.3633 | 141.6088 | 157.01 | 40.9408 | 0.78051 | 1.1826 | 0.050175
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 142.576 | 158.9154 | 0.95423 | 6.18 | -0.18117 | 862.9459
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 142.2313 | 1.803 | 0.023 | 6.18 | -0.49755 | 896.6569
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0 | 142.9318 | 0.83 | 0.023 | 33.9825 | 1.3084 | 1038.853
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.016908 | 143.4013 | 0.83 | 0.023 | 26.6293 | 4.3057 | 1048.434
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.050723 | 143.1827 | 0.83 | 0.023 | 19.0397 | 7.5565 | 1038.186
CH_PLANT | Tampines 1 | 29/7/2024 3:00:00 pm | 0.050723 | 141.9587 | 0.83 | 0.023 | 11.2898 | 9.063 | 1040.852
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.14088 | 139.8857 | 0.83 | 0.028 | 8.9551 | 9.6894 | 1058.503
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.14088 | 141.27 | 0.83 | 0.028 | 6.7642 | 12.821 | 1024.989
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.14088 | 141.7941 | 0.83 | 0.028 | 8.3708 | 15.5577 | 1065.603
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.14088 | 211.3907 | 0.83 | 0.028 | 8.4711 | 15.6908 | 1068.949
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.12797 | 125.0453 | 0.83 | 0.028 | 7.1738 | 25.7542 | 1064.135
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.088215 | 122.1157 | 0.83 | 0.028 | 10.6001 | -0.098259 | 870.7095
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 224.4682 | 134.7627 | 1.821 | 36.8521 | 4.5268 | -0.14402 | 900.9366
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 372.8486 | 142.0195 | 350.1997 | 70.7896 | 0.76155 | 0.33319 | 907.2243
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 227.3992 | 141.0818 | 281.2738 | 42.8775 | 0.68755 | -0.083678 | 893.1748
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 254.9916 | 144.3085 | 175.87 | 41.1297 | 0.62809 | -0.099753 | 1039.508
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 255.8372 | 143.05 | 160.6298 | 40.9786 | 0.6242 | 0.76645 | 1030.996
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 255.2364 | 144.1205 | 157.7287 | 41.0366 | 0.62774 | 6.3262 | 1043.581
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 255.3587 | 144.5835 | 159.88 | 41.0893 | 0.63871 | 6.7394 | 1031.573
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 252.129 | 265.318 | 160.2983 | 40.996 | 0.63407 | 12.6395 | 1058.812
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 252.737 | 247.75 | 160.0222 | 40.9035 | 0.64034 | 18.9155 | 1063.401
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 256.828 | 127.7817 | 164.0948 | 41.1374 | 0.62836 | 20.4281 | 1057.548
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 258.7526 | 280.6798 | 160.5053 | 40.9563 | 0.6121 | 21.0207 | 871.9294
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 256.1333 | 235.2458 | 162.7955 | 41.0798 | 0.62325 | 28.5815 | 943.1224
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 237.4005 | 168.3037 | 162.3 | 41.331 | 0.63779 | 21.9881 | 1033.666
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 248.3295 | 145.1907 | 158.752 | 40.771 | 0.69522 | 0.029592 | 1056.056
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 142.3572 | 1.8103 | 0.78508 | 2.3258 | -0.15671 | 1061.255
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 143.2948 | 0.83 | 0.027 | 2.3258 | -0.10205 | 1041.611
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 143.8213 | 0.83 | 0.027 | 60.3223 | -0.61256 | 1036.183
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.030105 | 143.0695 | 0.83 | 0.027 | 28.2539 | -0.65419 | 1048.572
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.051609 | 143.0172 | 0.83 | 0.027 | 11.6679 | -0.56783 | 1050.892
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.09993 | 144.2282 | 0.83 | 0.027 | 10.9317 | 1.5811 | 1067.901
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10247 | 142.4952 | 0.83 | 0.027 | 9.8918 | 2.781 | 1066.451
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10351 | 146.19 | 0.83 | 0.025433 | 7.504 | 4.1667 | 1164.098
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10865 | 137.2217 | 0.83 | 0.025 | 9.4065 | 7.3829 | 1024.813
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.1146 | 0.83 | 0.83 | 0.025 | 6.7286 | 9.0097 | 1033.186
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.1146 | 0.83 | 0.83 | 0.025 | 7.1923 | 12.269 | 1037.898
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 7.0146 | 0.83 | 1.566 | 1.2336 | 8.6973 | 13.1164 | 1048.092
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 463.3467 | 0.83 | 257.5662 | 72.6787 | 0.91059 | 20.5579 | 1025.973
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 381.585 | 0.83 | 141.2028 | 72.349 | 0.73698 | -0.068321 | 1036.719
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 264.8494 | 0.83 | 159.5533 | 48.2704 | 0.71584 | -0.096173 | 1041.856
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 249.5523 | 0.82 | 160.7277 | 40.9349 | 0.64356 | 1.2825 | 1046.74
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 249.3424 | 0.82 | 161.6722 | 40.8956 | 0.64135 | -0.0037894 | 1051.684
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 250.0159 | 0.82 | 161.3202 | 40.8453 | 0.63981 | -0.059149 | 1006.404
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 249.2176 | 0.82 | 162.0658 | 40.8835 | 0.64295 | 2.6875 | 985.1463
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 251.831 | 0.82 | 162.4497 | 40.993 | 0.63405 | 4.0545 | 1051.923
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 252.5093 | 0.82 | 162.3155 | 40.877 | 0.65094 | 4.5709 | 1026.88
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 254.2031 | 0.82 | 161.0215 | 40.8466 | 0.62832 | 9.3657 | 1033.496
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 256.3384 | 0.82 | 158.8972 | 41.0233 | 0.63474 | 10.2887 | 1031.245
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 234.9592 | 0.82 | 160.46 | 40.302 | 0.65138 | 12.2243 | 1031.94
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 245.2163 | 0.82 | 160.8549 | 40.8383 | 1.5193 | 15.2955 | 1032.83
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 1.8115 | 0.80522 | 50.4839 | 15.2891 | 1031.736
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.83 | 0.029067 | 50.4839 | 15.1245 | 1047.3
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.83 | 0.02285 | 58.4958 | -0.074615 | 1066.75
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.011353 | 0.82 | 0.83 | 0.023167 | 33.253 | -0.14985 | 1059.366
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.052398 | 0.82 | 0.83 | 0.023 | 15.5205 | -0.33667 | 859.2554
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.057491 | 0.82 | 0.83 | 0.023 | 11.1049 | -0.51807 | 924.161
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10333 | 0.82 | 0.83 | 0.023 | 11.9385 | -0.53118 | 908.1718
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10333 | 0.82 | 0.83 | 0.023 | 8.348 | 0.85671 | 925.0761
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10333 | 0.82 | 0.83 | 0.023 | 10.1424 | 3.8126 | 992.4328
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10333 | 0.82 | 0.83 | 0.023 | 7.7654 | 4.9252 | 1029.748
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10667 | 0.82 | 0.83 | 0.023917 | 7.3475 | 519.5868 | 1046.874
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 2.5403 | 0.82 | 1.606 | 1.2107 | 9.0175 | 519.5868 | 1027.061
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 365.3462 | 0.82 | 247.0683 | 69.8127 | 0.70746 | 519.5868 | 1043.921
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 212.3759 | 0.82 | 144.425 | 40.7521 | 0.66427 | 519.5868 | 1726.136
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 249.7807 | 0.82 | 141.3698 | 40.903 | 0.63797 | 474.4282 | 1529.332
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 247.3195 | 0.82 | 153.9807 | 40.8578 | 0.64983 | 335.3918 | 857.3879
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 250.1599 | 0.82 | 161.1778 | 40.837 | 0.64628 | 162.0615 | 972.3392
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 249.7924 | 0.82 | 160.195 | 40.8798 | 0.64557 | -0.16663 | 1018.362
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 247.8874 | 0.82 | 163.2928 | 40.927 | 0.65392 | -0.16247 | 1038.569
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 246.8563 | 0.82 | 162.1948 | 40.8882 | 0.65862 | 0.09563 | 1022.918
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 247.3745 | 0.82 | 163.2433 | 40.9517 | 0.65602 | -0.38016 | 1011.85
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 253.4572 | 0.82 | 164.0872 | 41.0271 | 0.63566 | -0.3892 | 1031.375
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 250.997 | 0.82 | 297.1015 | 40.9806 | 0.63438 | 2.006 | 1020.958
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 232.9099 | 0.82 | 392.14 | 42.115 | 0.63067 | 4.7174 | 1044.704
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 255.1449 | 0.82 | 147.4105 | 40.8536 | 0.7504 | 10.5061 | 1039.928
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 1.6167 | 0.79662 | 4.3689 | 10.778 | 1039.508
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 1.6783 | 0.029 | 4.3689 | 10.8413 | 917.033
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 315.7033 | 0.029 | 27.4066 | 11.3776 | 1043.856
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.003336 | 0.82 | 269.4812 | 0.029 | 36.4171 | 12.0136 | 1068.608
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.050039 | 0.82 | 194.1592 | 0.029 | 15.7932 | 12.0136 | 1062.827
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.06097 | 0.82 | 164.454 | 0.029 | 12.5621 | 13.5211 | 1061.97
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10133 | 0.82 | 161.5215 | 0.029 | 12.1175 | -0.10711 | 1049.042
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10133 | 0.82 | 162.4512 | 0.029 | 8.293 | -0.16377 | 1058.536
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.10133 | 0.82 | 163.0525 | 0.029 | 10.2453 | -0.26544 | 1069.365
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.11248 | 0.82 | 162.2298 | 0.029 | 7.0494 | -0.65973 | 1080.882
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0.14652 | 0.82 | 161.6363 | 0.029 | 7.4736 | -0.75466 | 1054.089
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 5.331 | 0.82 | 161.6212 | 1.2184 | 8.4863 | -0.22711 | 1033.741
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 351.8589 | 0.82 | 159.6117 | 67.4144 | 0.70809 | 1.9337 | 1645.933
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 212.4667 | 0.82 | 163.45 | 40.6611 | 0.67958 | 2.7027 | 1089.653
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 210.0121 | 0.82 | 154.4307 | 40.472 | 0.67429 | 6.4673 | 1035.09
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 237.0269 | 0.82 | 1.6485 | 40.7071 | 0.64985 | 7.6585 | 1037.43
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 252.6357 | 0.82 | 0.83 | 40.8074 | 0.63741 | 9.1501 | 1046.247
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 251.0287 | 0.82 | 0.83 | 40.9122 | 0.63806 | 11.7132 | 1048.535
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 253.9387 | 0.82 | 0.83 | 40.9128 | 0.64486 | 16.0617 | 1057.161
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 249.9102 | 0.82 | 0.83 | 40.9515 | 0.64904 | 19.4863 | 1053.772
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 248.2321 | 0.82 | 0.83 | 40.9115 | 0.65838 | -0.13261 | 1061.198
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 256.5224 | 0.82 | 0.82 | 44.5145 | 0.64225 | -0.15931 | 1067.24
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 396.3681 | 0.82 | 0.82 | 72.1615 | 0.75068 | -0.15236 | 1080.798
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 211.2007 | 0.82 | 0.82 | 71.379 | 1.2173 | -0.43905 | 864.3814
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 323.2855 | 0.82 | 0.82 | 44.9245 | 0.76314 | -0.47467 | 1024.406
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.75627 | 4.453 | -0.24711 | 1039.213
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 3.4996 | 1053.893
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 4.627 | 1045.208
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.611
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1028.992
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.406
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 8.8144 | 1051.324
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 11.5816 | 1049.278
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | 15.2228 | 1055.082
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 4.453 | -0.094059 | 877.9323
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.026 | 17.1926 | -0.12636 | 884.2773
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 5.731 | 0.82 | 0.82 | 1.2471 | 51.037 | -0.022934 | 970.1237
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 453.2346 | 0.82 | 0.82 | 72.5447 | 0.69187 | -0.2911 | 1061.106
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 362.744 | 0.82 | 0.82 | 72.2521 | 0.74228 | -0.33163 | 1058.15
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 277.8152 | 0.82 | 0.82 | 53.7303 | 0.69685 | -0.32213 | 1056.86
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 248.9746 | 0.82 | 0.82 | 40.9114 | 0.65995 | -0.32213 | 1040.489
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 247.4081 | 0.82 | 0.82 | 40.9621 | 0.65312 | -0.22594 | 1033.822
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 249.8414 | 0.82 | 0.82 | 40.9006 | 0.65033 | -0.059809 | 1071.282
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 248.2441 | 0.82 | 0.82 | 40.934 | 0.65789 | -0.29741 | 1727.56
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 246.6658 | 0.82 | 0.82 | 40.9187 | 0.65846 | -0.30991 | 1539.706
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 247.5377 | 0.82 | 0.82 | 40.9878 | 0.65259 | -0.30991 | 1561.595
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 250.6421 | 0.82 | 0.82 | 40.8562 | 0.64558 | -0.25927 | 1158.264
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 248.7138 | 0.82 | 0.82 | 40.9364 | 0.64336 | 0.72283 | 1033.918
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 224.9341 | 0.82 | 0.82 | 40.757 | 0.66113 | -0.040134 | 1032.46
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 245.7537 | 0.82 | 0.82 | 40.7378 | 0.70649 | -0.16181 | 1046.441
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.79742 | 1.9423 | -0.22997 | 1036.824
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48001 | 1024.879
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.56223 | 1042.816
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48538 | 1045.783
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1039.836
CH_PLANT | Century Square | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1043.321
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 5.731 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 453.2346 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 362.744 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 277.8152 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 248.9746 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 247.4081 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 249.8414 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 248.2441 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 246.6658 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 247.5377 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 250.6421 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 248.7138 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 224.9341 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 245.7537 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 0 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.9868 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.9167 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.8466 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.7765 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.7064 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.6362 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.5661 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.496 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.4259 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.3558 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.2857 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.2156 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.1455 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.0754 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 128.0053 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.9352 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.865 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.7949 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.7248 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.6547 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.5846 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.5145 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.4444 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.3743 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.3042 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.2341 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.164 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.0938 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 127.0237 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.9536 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.8835 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.8134 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.7433 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.6732 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.6031 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.533 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.4629 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.3927 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.3226 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.2525 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.1824 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.1123 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 126.0422 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.9721 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.902 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.8319 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.7618 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.6917 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.6215 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.5514 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.4813 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.4112 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.3411 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.271 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.2009 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.1308 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 125.0607 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.9906 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.9204 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.8503 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.7802 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.7101 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.64 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.5699 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.4998 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.4297 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.3596 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.2895 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.2194 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.1492 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.0791 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 124.009 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.9389 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.8688 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.7987 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.7286 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.6585 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.5884 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.5183 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.4482 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.378 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.3079 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.2378 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.1677 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.0976 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 123.0275 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.9574 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.8873 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.8172 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.7471 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.6769 | 131.7272 | 159.2118 | 41.079 | 0.62344 | -0.10051 | 0.040715
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.6068 | 139.838 | 159.4572 | 40.9576 | 0.63158 | -0.10622 | 0.037693
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.5367 | 142.3787 | 156.58 | 40.127 | 0.65917 | -0.059145 | 0.037693
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.4666 | 142.9808 | 159.9854 | 40.9299 | 0.67922 | -0.084936 | 0.037693
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.3965 | 141.9497 | 150.8555 | 40.908 | 0.69374 | -0.10325 | 0.035985
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.3264 | 142.9197 | 138.1777 | 40.916 | 0.69775 | -0.10198 | 0.027444
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.2563 | 141.6483 | 6.752 | 3.4926 | 83.086 | -0.10838 | 0.027444
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.1862 | 137.604 | 0.84 | 0.027 | 100 | -0.11046 | 0.027444
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.1161 | 140.7528 | 0.84 | 0.027 | 100 | -0.10784 | 5.3268
CH_PLANT | White Sands | 29/7/2024 3:00:00 pm | 122.046 | 136.84 | 0.84 | 0.027 | 100 | -0.11336 | 1989.365
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.9759 | 141.4985 | 1.23 | 0.024 | 6.6646 | -0.11491 | 1021.944
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.9057 | 0.83 | 1.23 | 0.024 | 7.3577 | -0.10588 | 0.549
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.8356 | 0.83 | 1.23 | 0.024 | 5.7515 | -0.11082 | 0.032093
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.7655 | 0.83 | 1.23 | 0.024 | 7.6403 | -0.13482 | 0.033581
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.6954 | 0.83 | 1.23 | 0.024 | 6.4198 | -0.08407 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.6253 | 0.83 | 1.23 | 0.024 | 5.6763 | -0.11678 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.5552 | 0.83 | 145.6395 | 36.886 | 4.3894 | -0.11124 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.4851 | 0.83 | 263.8778 | 70.8171 | 0.74909 | -0.11493 | 0.028869
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.415 | 0.83 | 143.6267 | 42.9785 | 0.68202 | -0.09018 | 0.020435
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.3449 | 0.83 | 150.3923 | 40.7452 | 0.66066 | -0.10321 | 0.018327
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.2748 | 0.83 | 157.531 | 40.9629 | 0.61277 | -0.11586 | 0.018327
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.2047 | 0.83 | 159.9617 | 40.9678 | 0.61821 | -0.10567 | 0.018327
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.1345 | 0.83 | 160.407 | 41.0693 | 0.6237 | -0.093901 | 2.9502
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 121.0644 | 280.394 | 159.2295 | 41.0961 | 0.62318 | -0.14155 | 1566.063
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.9943 | 170.7897 | 160.1795 | 41.1538 | 0.63567 | -0.20497 | 1005.043
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.9242 | 142.1868 | 158.8533 | 41.0918 | 0.62736 | -0.077332 | 0.57226
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.8541 | 140.9953 | 154.8203 | 41.0734 | 0.60607 | -0.093229 | 0.061741
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.784 | 141.3117 | 158.0203 | 41.1464 | 0.60867 | -0.10299 | 0.074108
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.7139 | 142.0145 | 153.75 | 40.447 | 0.62025 | -0.10932 | 0.06796
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.6438 | 142.7058 | 158.8163 | 40.9356 | 0.65941 | -0.093705 | 0.061262
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.5737 | 139.9993 | 1.7892 | 1.4081 | 15.9491 | -0.092 | 0.056499
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.5036 | 139.8698 | 1.46 | 0.024 | 15.9491 | -0.10716 | 0.048864
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.4334 | 140.4943 | 314.0868 | 0.024 | 33.2896 | -0.10601 | 0.046605
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.3633 | 138.0458 | 192.8402 | 0.024 | 25.2073 | -0.097927 | 0.038783
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.2932 | 135.91 | 159.6322 | 0.024 | 16.7405 | -0.10611 | 0.029609
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.2231 | 142.3993 | 158.3218 | 0.024 | 9.9003 | -0.13031 | 0.027377
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.153 | 221.4172 | 158.681 | 0.024 | 12.0921 | -0.076295 | 7.2576
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.0829 | 137.7345 | 159.248 | 0.024 | 8.3197 | -0.10132 | 1667.161
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 120.0128 | 144.3753 | 159.9183 | 0.024 | 7.8482 | -0.11949 | 961.0121
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.9427 | 143.3145 | 157.141 | 0.024 | 8.5625 | -0.11649 | 0.26549
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.8726 | 142.7942 | 157.0072 | 0.024 | 6.1329 | -0.11532 | 0.048098
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.8025 | 142.8697 | 157.6587 | 1.2388 | 7.6569 | -0.11547 | 0.052442
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.7324 | 143.6523 | 155.0962 | 72.8287 | 0.67636 | -0.12133 | 0.052442
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.6622 | 144.2565 | 153.18 | 50.2432 | 0.67834 | -0.11666 | 0.046237
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.5921 | 143.0503 | 159.5095 | 41.0497 | 0.63689 | -0.11995 | 0.041877
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.522 | 141.0682 | 1.8083 | 41.0843 | 0.62837 | -0.10615 | 0.037509
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.4519 | 144.078 | 0.84 | 41.1265 | 0.62826 | -0.11515 | 0.037509
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.3818 | 145.99 | 0.84 | 40.9531 | 0.6288 | -0.13933 | 0.033416
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.3117 | 140.0364 | 0.84 | 41.0044 | 0.6375 | -0.096132 | 0.026347
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.2416 | 1.2 | 0.84 | 41.0585 | 0.6279 | -0.11237 | 0.026347
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.1715 | 1.2 | 0.84 | 41.0366 | 0.62291 | -0.11498 | 3.4504
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.1014 | 1.2 | 0.84 | 40.9098 | 0.61563 | -0.12037 | 1666.068
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 119.0313 | 1.2 | 0.84 | 41.0441 | 0.60789 | -0.12485 | 1008.752
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.9611 | 1.2 | 0.84 | 42.061 | 0.58872 | -0.12308 | 0.41415
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.891 | 1.2 | 0.84 | 40.914 | 0.68759 | -0.11821 | 0.049389
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.8209 | 1.2 | 0.84 | 1.4067 | 21.9641 | -0.11876 | 0.049699
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.7508 | 1.2 | 1.2152 | 0.027117 | 21.9641 | -0.1167 | 0.044414
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.6807 | 1.2 | 250.7245 | 0.029483 | 34.4065 | -0.16476 | 0.042329
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.6106 | 1.2 | 157.5758 | 0.02985 | 26.4288 | -0.086652 | 0.033989
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.5405 | 1.2 | 161.7642 | 0.03025 | 20.06 | -0.10189 | 0.001006
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.4704 | 1.2 | 160.5303 | 0.03 | 10.5145 | -0.12355 | 0.001006
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.4003 | 240.5975 | 159.9868 | 0.029833 | 10.3076 | -0.12614 | 0.001006
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.3302 | 124.592 | 159.9677 | 0.029833 | 9.8666 | -0.12018 | 0.001006
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.2601 | 136.7727 | 160.8637 | 0.028783 | 7.3602 | -0.11768 | 0.001006
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.1899 | 131.7778 | 161.479 | 0.030667 | 9.7727 | -0.11644 | 0.001006
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.1198 | 136.76 | 160.0555 | 0.030167 | 6.3896 | -0.11919 | 1009.799
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 118.0497 | 140.0172 | 158.195 | 0.69977 | 7.0595 | -0.11297 | 1671.116
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.9796 | 143.072 | 161.273 | 61.9782 | 0.66109 | -0.11959 | 1036.345
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.9095 | 142.5625 | 162.53 | 45.4487 | 0.65936 | -0.10959 | 0.24878
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.8394 | 142.6107 | 157.0676 | 41.1473 | 0.63108 | -0.10163 | 0.045289
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.7693 | 145.348 | 2.1613 | 41.0763 | 0.64021 | -0.1187 | 0.044205
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.6992 | 265.565 | 1.23 | 41.0747 | 0.63828 | -0.097798 | 0.044205
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.6291 | 239.71 | 1.23 | 41.1149 | 0.64312 | -0.12404 | 0.037228
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.559 | 143.6597 | 1.23 | 41.0748 | 0.64221 | -0.12684 | 0.032892
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.4889 | 244.3348 | 1.23 | 41.0344 | 0.64824 | -0.11608 | 0.032892
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.4187 | 128.6923 | 1.23 | 41.0037 | 0.6462 | -0.11577 | 0.032892
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.3486 | 141.4727 | 1.23 | 41.1388 | 0.621 | -0.11551 | 0.032892
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.2785 | 142.4573 | 1.23 | 41.1382 | 0.62535 | -0.10978 | 0.032892
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.2084 | 140.9642 | 1.23 | 40.495 | 0.63516 | -0.14848 | 0.032892
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.1383 | 143.3018 | 1.23 | 40.8738 | 0.73453 | -0.21519 | 5.9819
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 117.0682 | 141.8913 | 1.23 | 1.2019 | 38.2672 | -0.13602 | 2016.554
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.9981 | 142.2788 | 1.9288 | 0.022833 | 38.2672 | -0.10063 | 1028.995
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.928 | 140.1968 | 276.5095 | 0.025517 | 38.2672 | -0.11335 | 0.46443
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.8579 | 141.3907 | 145.4742 | 0.02915 | 47.7725 | -0.11737 | 0.087425
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.7878 | 140.492 | 156.0923 | 0.029017 | 25.0666 | -0.12104 | 0.093489
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.7176 | 139.35 | 151.097 | 0.028836 | 12.7812 | -0.1182 | 0.082881
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.6475 | 141.1839 | 155.9507 | 0.024383 | 11.9719 | -0.11327 | 0.071217
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.5774 | 121.194 | 159.256 | 0.023433 | 11.6415 | -0.12573 | 0.062294
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.5073 | 248.875 | 162.1848 | 0.024667 | 8.6229 | -0.1179 | 0.051746
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.4372 | 134.2565 | 160.167 | 0.022583 | 12.1001 | -0.11933 | 0.045209
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.3671 | 140.4328 | 159.955 | 0.0215 | 8.3245 | -0.13251 | 0.038586
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.297 | 140.6595 | 163.0452 | 1.192 | 9.7423 | -0.55642 | 0.030394
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.2269 | 141.4652 | 298.5412 | 71.062 | 0.71877 | -0.48945 | 0.024451
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.1568 | 143.8553 | 271.85 | 42.7672 | 0.70324 | -0.32384 | 9.7405
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.0867 | 140.671 | 164.7647 | 40.6946 | 0.70861 | -0.18545 | 1621.899
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 116.0166 | 142.5722 | 1.6623 | 40.6721 | 0.69414 | 0.20734 | 1012.545
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.9464 | 142.0108 | 1.4982 | 40.6807 | 0.70578 | 0.58086 | 0.48901
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.8763 | 138.9657 | 278.581 | 41.0242 | 0.65144 | 1.3976 | 0.052207
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.8062 | 140.1183 | 149.3538 | 41.0311 | 0.64721 | 0.013006 | 0.055203
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.7361 | 137.84 | 160.7307 | 41.0917 | 0.63682 | -0.14062 | 0.054199
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.666 | 139.6983 | 161.7633 | 41.0286 | 0.63863 | -0.14404 | 0.045992
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.5959 | 283.4212 | 160.2337 | 44.2278 | 0.63777 | -0.1109 | 0.043262
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.5258 | 246.3632 | 162.5527 | 72.3453 | 0.74366 | 0.081825 | 0.043262
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.4557 | 152.9748 | 161.0952 | 71.715 | 0.83632 | -0.11574 | 0.043262
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.3856 | 141.4663 | 161.5225 | 48.1943 | 0.71517 | -0.2866 | 0.043262
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.3155 | 138.5828 | 159.4928 | 0.90082 | 83.5189 | -0.2866 | 0.043262
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.2453 | 140.726 | 160.5523 | 0.0267 | 93.2616 | -0.2866 | 0.043262
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.1752 | 141.1152 | 159.5868 | 0.029 | 56.1047 | -0.067319 | 6.3709
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.1051 | 140.76 | 157.33 | 0.029 | 17.6902 | 0.034298 | 1553.082
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 115.035 | 145.1577 | 158.5388 | 0.029 | 17.1311 | 0.034298 | 900.5404
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.9649 | 141.3635 | 1.6907 | 0.029 | 10.3691 | 0.034298 | 0.32157
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.8948 | 143.7097 | 1.25 | 0.029 | 12.119 | 0.023504 | 0.039287
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.8247 | 143.32 | 1.25 | 0.029 | 9.429 | 0.13675 | 0.039036
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.7546 | 139.692 | 1.25 | 0.029 | 8.9298 | -0.14278 | 0.038355
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.6845 | 0.83 | 1.25 | 0.029 | 10.0366 | -0.13003 | 0.038355
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.6144 | 0.83 | 1.25 | 0.028833 | 7.0211 | -0.1194 | 0.034431
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.5443 | 0.83 | 1.25 | 1.2127 | 9.1607 | 0.081239 | 0.027654
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.4741 | 0.83 | 142.9307 | 70.9289 | 0.73104 | -0.2202 | 0.037175
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.404 | 0.83 | 283.9762 | 42.8245 | 0.70969 | -0.33499 | 0.037677
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.3339 | 0.83 | 155.5683 | 40.9779 | 0.67503 | -0.33499 | 0.037677
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.2638 | 0.83 | 159.8705 | 40.9816 | 0.65245 | 135.4711 | 0.035654
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.1937 | 0.83 | 159.8542 | 41.0895 | 0.63801 | 135.4711 | 5.7509
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.1236 | 0.83 | 160.6118 | 41.0359 | 0.64496 | 135.4711 | 1944.854
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 114.0535 | 0.83 | 163.082 | 41.1324 | 0.64728 | 135.4711 | 983.0244
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.9834 | 0.83 | 159.8013 | 41.0387 | 0.64627 | 135.4711 | 0.32158
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.9133 | 0.83 | 161.696 | 41.1871 | 0.64315 | 135.4711 | 0.05447
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.8432 | 222.2117 | 161.149 | 41.0378 | 0.62559 | 65.4282 | 0.062073
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.7731 | 121.7788 | 158.0473 | 41.1095 | 0.63305 | -0.15394 | 0.052725
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.7029 | 140.3862 | 159.2922 | 41.106 | 0.63221 | -0.14521 | 0.050175
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.6328 | 141.6088 | 157.01 | 40.9408 | 0.78051 | 1.1826 | 0.050175
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.5627 | 142.576 | 158.9154 | 0.95423 | 6.18 | -0.18117 | 862.9459
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.4926 | 142.2313 | 1.803 | 0.023 | 6.18 | -0.49755 | 896.6569
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.4225 | 142.9318 | 0.83 | 0.023 | 33.9825 | 1.3084 | 1038.853
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.3524 | 143.4013 | 0.83 | 0.023 | 26.6293 | 4.3057 | 1048.434
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.2823 | 143.1827 | 0.83 | 0.023 | 19.0397 | 7.5565 | 1038.186
CH_PLANT | Hougang Mall | 29/7/2024 3:00:00 pm | 113.2122 | 141.9587 | 0.83 | 0.023 | 11.2898 | 9.063 | 1040.852
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 113.1421 | 139.8857 | 0.83 | 0.028 | 8.9551 | 9.6894 | 1058.503
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 113.072 | 141.27 | 0.83 | 0.028 | 6.7642 | 12.821 | 1024.989
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 113.0018 | 141.7941 | 0.83 | 0.028 | 8.3708 | 15.5577 | 1065.603
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.9317 | 211.3907 | 0.83 | 0.028 | 8.4711 | 15.6908 | 1068.949
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.8616 | 125.0453 | 0.83 | 0.028 | 7.1738 | 25.7542 | 1064.135
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.7915 | 122.1157 | 0.83 | 0.028 | 10.6001 | -0.098259 | 870.7095
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.7214 | 134.7627 | 1.821 | 36.8521 | 4.5268 | -0.14402 | 900.9366
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.6513 | 142.0195 | 350.1997 | 70.7896 | 0.76155 | 0.33319 | 907.2243
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.5812 | 141.0818 | 281.2738 | 42.8775 | 0.68755 | -0.083678 | 893.1748
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.5111 | 144.3085 | 175.87 | 41.1297 | 0.62809 | -0.099753 | 1039.508
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.441 | 143.05 | 160.6298 | 40.9786 | 0.6242 | 0.76645 | 1030.996
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.3709 | 144.1205 | 157.7287 | 41.0366 | 0.62774 | 6.3262 | 1043.581
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.3008 | 144.5835 | 159.88 | 41.0893 | 0.63871 | 6.7394 | 1031.573
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.2306 | 265.318 | 160.2983 | 40.996 | 0.63407 | 12.6395 | 1058.812
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.1605 | 247.75 | 160.0222 | 40.9035 | 0.64034 | 18.9155 | 1063.401
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.0904 | 127.7817 | 164.0948 | 41.1374 | 0.62836 | 20.4281 | 1057.548
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 112.0203 | 280.6798 | 160.5053 | 40.9563 | 0.6121 | 21.0207 | 871.9294
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.9502 | 235.2458 | 162.7955 | 41.0798 | 0.62325 | 28.5815 | 943.1224
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.8801 | 168.3037 | 162.3 | 41.331 | 0.63779 | 21.9881 | 1033.666
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.81 | 145.1907 | 158.752 | 40.771 | 0.69522 | 0.029592 | 1056.056
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.7399 | 142.3572 | 1.8103 | 0.78508 | 2.3258 | -0.15671 | 1061.255
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.6698 | 143.2948 | 0.83 | 0.027 | 2.3258 | -0.10205 | 1041.611
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.5997 | 143.8213 | 0.83 | 0.027 | 60.3223 | -0.61256 | 1036.183
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.5296 | 143.0695 | 0.83 | 0.027 | 28.2539 | -0.65419 | 1048.572
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.4594 | 143.0172 | 0.83 | 0.027 | 11.6679 | -0.56783 | 1050.892
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.3893 | 144.2282 | 0.83 | 0.027 | 10.9317 | 1.5811 | 1067.901
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.3192 | 142.4952 | 0.83 | 0.027 | 9.8918 | 2.781 | 1066.451
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.2491 | 146.19 | 0.83 | 0.025433 | 7.504 | 4.1667 | 1164.098
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.179 | 137.2217 | 0.83 | 0.025 | 9.4065 | 7.3829 | 1024.813
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.1089 | 0.83 | 0.83 | 0.025 | 6.7286 | 9.0097 | 1033.186
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 111.0388 | 0.83 | 0.83 | 0.025 | 7.1923 | 12.269 | 1037.898
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.9687 | 0.83 | 1.566 | 1.2336 | 8.6973 | 13.1164 | 1048.092
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.8986 | 0.83 | 257.5662 | 72.6787 | 0.91059 | 20.5579 | 1025.973
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.8285 | 0.83 | 141.2028 | 72.349 | 0.73698 | -0.068321 | 1036.719
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.7583 | 0.83 | 159.5533 | 48.2704 | 0.71584 | -0.096173 | 1041.856
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.6882 | 0.82 | 160.7277 | 40.9349 | 0.64356 | 1.2825 | 1046.74
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.6181 | 0.82 | 161.6722 | 40.8956 | 0.64135 | -0.0037894 | 1051.684
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.548 | 0.82 | 161.3202 | 40.8453 | 0.63981 | -0.059149 | 1006.404
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.4779 | 0.82 | 162.0658 | 40.8835 | 0.64295 | 2.6875 | 985.1463
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.4078 | 0.82 | 162.4497 | 40.993 | 0.63405 | 4.0545 | 1051.923
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.3377 | 0.82 | 162.3155 | 40.877 | 0.65094 | 4.5709 | 1026.88
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.2676 | 0.82 | 161.0215 | 40.8466 | 0.62832 | 9.3657 | 1033.496
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.1975 | 0.82 | 158.8972 | 41.0233 | 0.63474 | 10.2887 | 1031.245
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.1274 | 0.82 | 160.46 | 40.302 | 0.65138 | 12.2243 | 1031.94
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 110.0573 | 0.82 | 160.8549 | 40.8383 | 1.5193 | 15.2955 | 1032.83
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.9871 | 0.82 | 1.8115 | 0.80522 | 50.4839 | 15.2891 | 1031.736
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.917 | 0.82 | 0.83 | 0.029067 | 50.4839 | 15.1245 | 1047.3
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.8469 | 0.82 | 0.83 | 0.02285 | 58.4958 | -0.074615 | 1066.75
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.7768 | 0.82 | 0.83 | 0.023167 | 33.253 | -0.14985 | 1059.366
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.7067 | 0.82 | 0.83 | 0.023 | 15.5205 | -0.33667 | 859.2554
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.6366 | 0.82 | 0.83 | 0.023 | 11.1049 | -0.51807 | 924.161
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.5665 | 0.82 | 0.83 | 0.023 | 11.9385 | -0.53118 | 908.1718
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.4964 | 0.82 | 0.83 | 0.023 | 8.348 | 0.85671 | 925.0761
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.4263 | 0.82 | 0.83 | 0.023 | 10.1424 | 3.8126 | 992.4328
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.3562 | 0.82 | 0.83 | 0.023 | 7.7654 | 4.9252 | 1029.748
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.286 | 0.82 | 0.83 | 0.023917 | 7.3475 | 519.5868 | 1046.874
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.2159 | 0.82 | 1.606 | 1.2107 | 9.0175 | 519.5868 | 1027.061
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.1458 | 0.82 | 247.0683 | 69.8127 | 0.70746 | 519.5868 | 1043.921
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.0757 | 0.82 | 144.425 | 40.7521 | 0.66427 | 519.5868 | 1726.136
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 109.0056 | 0.82 | 141.3698 | 40.903 | 0.63797 | 474.4282 | 1529.332
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.9355 | 0.82 | 153.9807 | 40.8578 | 0.64983 | 335.3918 | 857.3879
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.8654 | 0.82 | 161.1778 | 40.837 | 0.64628 | 162.0615 | 972.3392
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.7953 | 0.82 | 160.195 | 40.8798 | 0.64557 | -0.16663 | 1018.362
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.7252 | 0.82 | 163.2928 | 40.927 | 0.65392 | -0.16247 | 1038.569
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.6551 | 0.82 | 162.1948 | 40.8882 | 0.65862 | 0.09563 | 1022.918
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.585 | 0.82 | 163.2433 | 40.9517 | 0.65602 | -0.38016 | 1011.85
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.5148 | 0.82 | 164.0872 | 41.0271 | 0.63566 | -0.3892 | 1031.375
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.4447 | 0.82 | 297.1015 | 40.9806 | 0.63438 | 2.006 | 1020.958
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.3746 | 0.82 | 392.14 | 42.115 | 0.63067 | 4.7174 | 1044.704
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.3045 | 0.82 | 147.4105 | 40.8536 | 0.7504 | 10.5061 | 1039.928
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.2344 | 0.82 | 1.6167 | 0.79662 | 4.3689 | 10.778 | 1039.508
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.1643 | 0.82 | 1.6783 | 0.029 | 4.3689 | 10.8413 | 917.033
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.0942 | 0.82 | 315.7033 | 0.029 | 27.4066 | 11.3776 | 1043.856
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 108.0241 | 0.82 | 269.4812 | 0.029 | 36.4171 | 12.0136 | 1068.608
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.954 | 0.82 | 194.1592 | 0.029 | 15.7932 | 12.0136 | 1062.827
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.8839 | 0.82 | 164.454 | 0.029 | 12.5621 | 13.5211 | 1061.97
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.8138 | 0.82 | 161.5215 | 0.029 | 12.1175 | -0.10711 | 1049.042
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.7436 | 0.82 | 162.4512 | 0.029 | 8.293 | -0.16377 | 1058.536
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.6735 | 0.82 | 163.0525 | 0.029 | 10.2453 | -0.26544 | 1069.365
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.6034 | 0.82 | 162.2298 | 0.029 | 7.0494 | -0.65973 | 1080.882
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.5333 | 0.82 | 161.6363 | 0.029 | 7.4736 | -0.75466 | 1054.089
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.4632 | 0.82 | 161.6212 | 1.2184 | 8.4863 | -0.22711 | 1033.741
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.3931 | 0.82 | 159.6117 | 67.4144 | 0.70809 | 1.9337 | 1645.933
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.323 | 0.82 | 163.45 | 40.6611 | 0.67958 | 2.7027 | 1089.653
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.2529 | 0.82 | 154.4307 | 40.472 | 0.67429 | 6.4673 | 1035.09
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.1828 | 0.82 | 1.6485 | 40.7071 | 0.64985 | 7.6585 | 1037.43
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.1127 | 0.82 | 0.83 | 40.8074 | 0.63741 | 9.1501 | 1046.247
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 107.0425 | 0.82 | 0.83 | 40.9122 | 0.63806 | 11.7132 | 1048.535
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.9724 | 0.82 | 0.83 | 40.9128 | 0.64486 | 16.0617 | 1057.161
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.9023 | 0.82 | 0.83 | 40.9515 | 0.64904 | 19.4863 | 1053.772
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.8322 | 0.82 | 0.83 | 40.9115 | 0.65838 | -0.13261 | 1061.198
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.7621 | 0.82 | 0.82 | 44.5145 | 0.64225 | -0.15931 | 1067.24
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.692 | 0.82 | 0.82 | 72.1615 | 0.75068 | -0.15236 | 1080.798
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.6219 | 0.82 | 0.82 | 71.379 | 1.2173 | -0.43905 | 864.3814
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.5518 | 0.82 | 0.82 | 44.9245 | 0.76314 | -0.47467 | 1024.406
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.4817 | 0.82 | 0.82 | 0.75627 | 4.453 | -0.24711 | 1039.213
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.4116 | 0.82 | 0.82 | 0.026 | 4.453 | 3.4996 | 1053.893
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.3415 | 0.82 | 0.82 | 0.026 | 4.453 | 4.627 | 1045.208
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.2713 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.611
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.2012 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1028.992
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.1311 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.406
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 106.061 | 0.82 | 0.82 | 0.026 | 4.453 | 8.8144 | 1051.324
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.9909 | 0.82 | 0.82 | 0.026 | 4.453 | 11.5816 | 1049.278
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.9208 | 0.82 | 0.82 | 0.026 | 4.453 | 15.2228 | 1055.082
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.8507 | 0.82 | 0.82 | 0.026 | 4.453 | -0.094059 | 877.9323
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.7806 | 0.82 | 0.82 | 0.026 | 17.1926 | -0.12636 | 884.2773
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.7105 | 0.82 | 0.82 | 1.2471 | 51.037 | -0.022934 | 970.1237
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.6404 | 0.82 | 0.82 | 72.5447 | 0.69187 | -0.2911 | 1061.106
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.5702 | 0.82 | 0.82 | 72.2521 | 0.74228 | -0.33163 | 1058.15
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.5001 | 0.82 | 0.82 | 53.7303 | 0.69685 | -0.32213 | 1056.86
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.43 | 0.82 | 0.82 | 40.9114 | 0.65995 | -0.32213 | 1040.489
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.3599 | 0.82 | 0.82 | 40.9621 | 0.65312 | -0.22594 | 1033.822
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.2898 | 0.82 | 0.82 | 40.9006 | 0.65033 | -0.059809 | 1071.282
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.2197 | 0.82 | 0.82 | 40.934 | 0.65789 | -0.29741 | 1727.56
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.1496 | 0.82 | 0.82 | 40.9187 | 0.65846 | -0.30991 | 1539.706
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.0795 | 0.82 | 0.82 | 40.9878 | 0.65259 | -0.30991 | 1561.595
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 105.0094 | 0.82 | 0.82 | 40.8562 | 0.64558 | -0.25927 | 1158.264
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.9393 | 0.82 | 0.82 | 40.9364 | 0.64336 | 0.72283 | 1033.918
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.8692 | 0.82 | 0.82 | 40.757 | 0.66113 | -0.040134 | 1032.46
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.799 | 0.82 | 0.82 | 40.7378 | 0.70649 | -0.16181 | 1046.441
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.7289 | 0.82 | 0.82 | 0.79742 | 1.9423 | -0.22997 | 1036.824
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.6588 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48001 | 1024.879
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.5887 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.56223 | 1042.816
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.5186 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48538 | 1045.783
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.4485 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1039.836
CH_PLANT | Waterway Point | 29/7/2024 3:00:00 pm | 104.3784 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1043.321
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 104.3083 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 104.2382 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 104.1681 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 104.098 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 104.0278 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.9577 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.8876 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.8175 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.7474 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.6773 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.6072 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.5371 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.467 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.3969 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.3267 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.2566 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.1865 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.1164 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 103.0463 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.9762 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.9061 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.836 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.7659 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.6958 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.6257 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.5555 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.4854 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.4153 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.3452 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.2751 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.205 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.1349 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 102.0648 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.9947 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.9246 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.8544 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.7843 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.7142 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.6441 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.574 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.5039 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.4338 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.3637 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.2936 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.2235 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.1534 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.0832 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 101.0131 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.943 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.8729 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.8028 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.7327 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.6626 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.5925 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.5224 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.4523 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.3822 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.312 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.2419 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.1718 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.1017 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 100.0316 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.9615 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.8914 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.8213 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.7512 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.6811 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.6109 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.5408 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.4707 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.4006 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.3305 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.2604 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.1903 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.1202 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 99.0501 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.98 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.9099 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.8397 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.7696 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.6995 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.6294 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.5593 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.4892 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.4191 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.349 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.2789 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.2088 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.1387 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 98.0685 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.9984 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.9283 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.8582 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.7881 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.718 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.6479 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.5778 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.5077 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.4376 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.3674 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.2973 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.2272 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.1571 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.087 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 97.0169 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.9468 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.8767 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.8066 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.7365 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.6664 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.5962 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.5261 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.456 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.3859 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.3158 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.2457 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.1756 | 131.7272 | 159.2118 | 41.079 | 0.62344 | -0.10051 | 0.040715
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.1055 | 139.838 | 159.4572 | 40.9576 | 0.63158 | -0.10622 | 0.037693
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 96.0354 | 142.3787 | 156.58 | 40.127 | 0.65917 | -0.059145 | 0.037693
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 95.9653 | 142.9808 | 159.9854 | 40.9299 | 0.67922 | -0.084936 | 0.037693
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 95.8951 | 141.9497 | 150.8555 | 40.908 | 0.69374 | -0.10325 | 0.035985
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 95.825 | 142.9197 | 138.1777 | 40.916 | 0.69775 | -0.10198 | 0.027444
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 95.7549 | 141.6483 | 6.752 | 3.4926 | 83.086 | -0.10838 | 0.027444
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 95.6848 | 137.604 | 0.84 | 0.027 | 100 | -0.11046 | 0.027444
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 95.6147 | 140.7528 | 0.84 | 0.027 | 100 | -0.10784 | 5.3268
CH_PLANT | North Point City (South Wing) | 29/7/2024 3:00:00 pm | 95.5446 | 136.84 | 0.84 | 0.027 | 100 | -0.11336 | 1989.365
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.4745 | 141.4985 | 1.23 | 0.024 | 6.6646 | -0.11491 | 1021.944
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.4044 | 0.83 | 1.23 | 0.024 | 7.3577 | -0.10588 | 0.549
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.3343 | 0.83 | 1.23 | 0.024 | 5.7515 | -0.11082 | 0.032093
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.2642 | 0.83 | 1.23 | 0.024 | 7.6403 | -0.13482 | 0.033581
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.1941 | 0.83 | 1.23 | 0.024 | 6.4198 | -0.08407 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.1239 | 0.83 | 1.23 | 0.024 | 5.6763 | -0.11678 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 95.0538 | 0.83 | 145.6395 | 36.886 | 4.3894 | -0.11124 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.9837 | 0.83 | 263.8778 | 70.8171 | 0.74909 | -0.11493 | 0.028869
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.9136 | 0.83 | 143.6267 | 42.9785 | 0.68202 | -0.09018 | 0.020435
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.8435 | 0.83 | 150.3923 | 40.7452 | 0.66066 | -0.10321 | 0.018327
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.7734 | 0.83 | 157.531 | 40.9629 | 0.61277 | -0.11586 | 0.018327
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.7033 | 0.83 | 159.9617 | 40.9678 | 0.61821 | -0.10567 | 0.018327
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.6332 | 0.83 | 160.407 | 41.0693 | 0.6237 | -0.093901 | 2.9502
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.5631 | 280.394 | 159.2295 | 41.0961 | 0.62318 | -0.14155 | 1566.063
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.493 | 170.7897 | 160.1795 | 41.1538 | 0.63567 | -0.20497 | 1005.043
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.4229 | 142.1868 | 158.8533 | 41.0918 | 0.62736 | -0.077332 | 0.57226
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.3527 | 140.9953 | 154.8203 | 41.0734 | 0.60607 | -0.093229 | 0.061741
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.2826 | 141.3117 | 158.0203 | 41.1464 | 0.60867 | -0.10299 | 0.074108
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.2125 | 142.0145 | 153.75 | 40.447 | 0.62025 | -0.10932 | 0.06796
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.1424 | 142.7058 | 158.8163 | 40.9356 | 0.65941 | -0.093705 | 0.061262
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.0723 | 139.9993 | 1.7892 | 1.4081 | 15.9491 | -0.092 | 0.056499
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 94.0022 | 139.8698 | 1.46 | 0.024 | 15.9491 | -0.10716 | 0.048864
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.9321 | 140.4943 | 314.0868 | 0.024 | 33.2896 | -0.10601 | 0.046605
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.862 | 138.0458 | 192.8402 | 0.024 | 25.2073 | -0.097927 | 0.038783
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.7919 | 135.91 | 159.6322 | 0.024 | 16.7405 | -0.10611 | 0.029609
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.7218 | 142.3993 | 158.3218 | 0.024 | 9.9003 | -0.13031 | 0.027377
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.6516 | 221.4172 | 158.681 | 0.024 | 12.0921 | -0.076295 | 7.2576
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.5815 | 137.7345 | 159.248 | 0.024 | 8.3197 | -0.10132 | 1667.161
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.5114 | 144.3753 | 159.9183 | 0.024 | 7.8482 | -0.11949 | 961.0121
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.4413 | 143.3145 | 157.141 | 0.024 | 8.5625 | -0.11649 | 0.26549
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.3712 | 142.7942 | 157.0072 | 0.024 | 6.1329 | -0.11532 | 0.048098
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.3011 | 142.8697 | 157.6587 | 1.2388 | 7.6569 | -0.11547 | 0.052442
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.231 | 143.6523 | 155.0962 | 72.8287 | 0.67636 | -0.12133 | 0.052442
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.1609 | 144.2565 | 153.18 | 50.2432 | 0.67834 | -0.11666 | 0.046237
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.0908 | 143.0503 | 159.5095 | 41.0497 | 0.63689 | -0.11995 | 0.041877
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 93.0207 | 141.0682 | 1.8083 | 41.0843 | 0.62837 | -0.10615 | 0.037509
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.9506 | 144.078 | 0.84 | 41.1265 | 0.62826 | -0.11515 | 0.037509
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.8804 | 145.99 | 0.84 | 40.9531 | 0.6288 | -0.13933 | 0.033416
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.8103 | 140.0364 | 0.84 | 41.0044 | 0.6375 | -0.096132 | 0.026347
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.7402 | 1.2 | 0.84 | 41.0585 | 0.6279 | -0.11237 | 0.026347
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.6701 | 1.2 | 0.84 | 41.0366 | 0.62291 | -0.11498 | 3.4504
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.6 | 1.2 | 0.84 | 40.9098 | 0.61563 | -0.12037 | 1666.068
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.5299 | 1.2 | 0.84 | 41.0441 | 0.60789 | -0.12485 | 1008.752
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.4598 | 1.2 | 0.84 | 42.061 | 0.58872 | -0.12308 | 0.41415
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.3897 | 1.2 | 0.84 | 40.914 | 0.68759 | -0.11821 | 0.049389
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.3196 | 1.2 | 0.84 | 1.4067 | 21.9641 | -0.11876 | 0.049699
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.2495 | 1.2 | 1.2152 | 0.027117 | 21.9641 | -0.1167 | 0.044414
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.1793 | 1.2 | 250.7245 | 0.029483 | 34.4065 | -0.16476 | 0.042329
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.1092 | 1.2 | 157.5758 | 0.02985 | 26.4288 | -0.086652 | 0.033989
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 92.0391 | 1.2 | 161.7642 | 0.03025 | 20.06 | -0.10189 | 0.001006
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.969 | 1.2 | 160.5303 | 0.03 | 10.5145 | -0.12355 | 0.001006
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.8989 | 240.5975 | 159.9868 | 0.029833 | 10.3076 | -0.12614 | 0.001006
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.8288 | 124.592 | 159.9677 | 0.029833 | 9.8666 | -0.12018 | 0.001006
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.7587 | 136.7727 | 160.8637 | 0.028783 | 7.3602 | -0.11768 | 0.001006
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.6886 | 131.7778 | 161.479 | 0.030667 | 9.7727 | -0.11644 | 0.001006
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.6185 | 136.76 | 160.0555 | 0.030167 | 6.3896 | -0.11919 | 1009.799
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.5484 | 140.0172 | 158.195 | 0.69977 | 7.0595 | -0.11297 | 1671.116
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.4783 | 143.072 | 161.273 | 61.9782 | 0.66109 | -0.11959 | 1036.345
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.4081 | 142.5625 | 162.53 | 45.4487 | 0.65936 | -0.10959 | 0.24878
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.338 | 142.6107 | 157.0676 | 41.1473 | 0.63108 | -0.10163 | 0.045289
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.2679 | 145.348 | 2.1613 | 41.0763 | 0.64021 | -0.1187 | 0.044205
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.1978 | 265.565 | 1.23 | 41.0747 | 0.63828 | -0.097798 | 0.044205
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.1277 | 239.71 | 1.23 | 41.1149 | 0.64312 | -0.12404 | 0.037228
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 91.0576 | 143.6597 | 1.23 | 41.0748 | 0.64221 | -0.12684 | 0.032892
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.9875 | 244.3348 | 1.23 | 41.0344 | 0.64824 | -0.11608 | 0.032892
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.9174 | 128.6923 | 1.23 | 41.0037 | 0.6462 | -0.11577 | 0.032892
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.8473 | 141.4727 | 1.23 | 41.1388 | 0.621 | -0.11551 | 0.032892
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.7772 | 142.4573 | 1.23 | 41.1382 | 0.62535 | -0.10978 | 0.032892
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.7071 | 140.9642 | 1.23 | 40.495 | 0.63516 | -0.14848 | 0.032892
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.6369 | 143.3018 | 1.23 | 40.8738 | 0.73453 | -0.21519 | 5.9819
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.5668 | 141.8913 | 1.23 | 1.2019 | 38.2672 | -0.13602 | 2016.554
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.4967 | 142.2788 | 1.9288 | 0.022833 | 38.2672 | -0.10063 | 1028.995
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.4266 | 140.1968 | 276.5095 | 0.025517 | 38.2672 | -0.11335 | 0.46443
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.3565 | 141.3907 | 145.4742 | 0.02915 | 47.7725 | -0.11737 | 0.087425
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.2864 | 140.492 | 156.0923 | 0.029017 | 25.0666 | -0.12104 | 0.093489
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.2163 | 139.35 | 151.097 | 0.028836 | 12.7812 | -0.1182 | 0.082881
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.1462 | 141.1839 | 155.9507 | 0.024383 | 11.9719 | -0.11327 | 0.071217
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.0761 | 121.194 | 159.256 | 0.023433 | 11.6415 | -0.12573 | 0.062294
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 90.006 | 248.875 | 162.1848 | 0.024667 | 8.6229 | -0.1179 | 0.051746
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.9358 | 134.2565 | 160.167 | 0.022583 | 12.1001 | -0.11933 | 0.045209
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.8657 | 140.4328 | 159.955 | 0.0215 | 8.3245 | -0.13251 | 0.038586
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.7956 | 140.6595 | 163.0452 | 1.192 | 9.7423 | -0.55642 | 0.030394
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.7255 | 141.4652 | 298.5412 | 71.062 | 0.71877 | -0.48945 | 0.024451
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.6554 | 143.8553 | 271.85 | 42.7672 | 0.70324 | -0.32384 | 9.7405
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.5853 | 140.671 | 164.7647 | 40.6946 | 0.70861 | -0.18545 | 1621.899
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.5152 | 142.5722 | 1.6623 | 40.6721 | 0.69414 | 0.20734 | 1012.545
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.4451 | 142.0108 | 1.4982 | 40.6807 | 0.70578 | 0.58086 | 0.48901
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.375 | 138.9657 | 278.581 | 41.0242 | 0.65144 | 1.3976 | 0.052207
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.3049 | 140.1183 | 149.3538 | 41.0311 | 0.64721 | 0.013006 | 0.055203
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.2348 | 137.84 | 160.7307 | 41.0917 | 0.63682 | -0.14062 | 0.054199
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.1646 | 139.6983 | 161.7633 | 41.0286 | 0.63863 | -0.14404 | 0.045992
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.0945 | 283.4212 | 160.2337 | 44.2278 | 0.63777 | -0.1109 | 0.043262
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 89.0244 | 246.3632 | 162.5527 | 72.3453 | 0.74366 | 0.081825 | 0.043262
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.9543 | 152.9748 | 161.0952 | 71.715 | 0.83632 | -0.11574 | 0.043262
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.8842 | 141.4663 | 161.5225 | 48.1943 | 0.71517 | -0.2866 | 0.043262
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.8141 | 138.5828 | 159.4928 | 0.90082 | 83.5189 | -0.2866 | 0.043262
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.744 | 140.726 | 160.5523 | 0.0267 | 93.2616 | -0.2866 | 0.043262
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.6739 | 141.1152 | 159.5868 | 0.029 | 56.1047 | -0.067319 | 6.3709
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.6038 | 140.76 | 157.33 | 0.029 | 17.6902 | 0.034298 | 1553.082
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.5337 | 145.1577 | 158.5388 | 0.029 | 17.1311 | 0.034298 | 900.5404
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.4636 | 141.3635 | 1.6907 | 0.029 | 10.3691 | 0.034298 | 0.32157
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.3934 | 143.7097 | 1.25 | 0.029 | 12.119 | 0.023504 | 0.039287
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.3233 | 143.32 | 1.25 | 0.029 | 9.429 | 0.13675 | 0.039036
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.2532 | 139.692 | 1.25 | 0.029 | 8.9298 | -0.14278 | 0.038355
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.1831 | 0.83 | 1.25 | 0.029 | 10.0366 | -0.13003 | 0.038355
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.113 | 0.83 | 1.25 | 0.028833 | 7.0211 | -0.1194 | 0.034431
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 88.0429 | 0.83 | 1.25 | 1.2127 | 9.1607 | 0.081239 | 0.027654
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.9728 | 0.83 | 142.9307 | 70.9289 | 0.73104 | -0.2202 | 0.037175
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.9027 | 0.83 | 283.9762 | 42.8245 | 0.70969 | -0.33499 | 0.037677
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.8326 | 0.83 | 155.5683 | 40.9779 | 0.67503 | -0.33499 | 0.037677
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.7625 | 0.83 | 159.8705 | 40.9816 | 0.65245 | 135.4711 | 0.035654
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.6923 | 0.83 | 159.8542 | 41.0895 | 0.63801 | 135.4711 | 5.7509
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.6222 | 0.83 | 160.6118 | 41.0359 | 0.64496 | 135.4711 | 1944.854
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.5521 | 0.83 | 163.082 | 41.1324 | 0.64728 | 135.4711 | 983.0244
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.482 | 0.83 | 159.8013 | 41.0387 | 0.64627 | 135.4711 | 0.32158
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.4119 | 0.83 | 161.696 | 41.1871 | 0.64315 | 135.4711 | 0.05447
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.3418 | 222.2117 | 161.149 | 41.0378 | 0.62559 | 65.4282 | 0.062073
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.2717 | 121.7788 | 158.0473 | 41.1095 | 0.63305 | -0.15394 | 0.052725
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.2016 | 140.3862 | 159.2922 | 41.106 | 0.63221 | -0.14521 | 0.050175
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.1315 | 141.6088 | 157.01 | 40.9408 | 0.78051 | 1.1826 | 0.050175
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 87.0614 | 142.576 | 158.9154 | 0.95423 | 6.18 | -0.18117 | 862.9459
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 86.9913 | 142.2313 | 1.803 | 0.023 | 6.18 | -0.49755 | 896.6569
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 86.9211 | 142.9318 | 0.83 | 0.023 | 33.9825 | 1.3084 | 1038.853
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 86.851 | 143.4013 | 0.83 | 0.023 | 26.6293 | 4.3057 | 1048.434
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 86.7809 | 143.1827 | 0.83 | 0.023 | 19.0397 | 7.5565 | 1038.186
CH_PLANT | The Centrepoint | 29/7/2024 3:00:00 pm | 86.7108 | 141.9587 | 0.83 | 0.023 | 11.2898 | 9.063 | 1040.852
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.6407 | 139.8857 | 0.83 | 0.028 | 8.9551 | 9.6894 | 1058.503
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.5706 | 141.27 | 0.83 | 0.028 | 6.7642 | 12.821 | 1024.989
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.5005 | 141.7941 | 0.83 | 0.028 | 8.3708 | 15.5577 | 1065.603
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.4304 | 211.3907 | 0.83 | 0.028 | 8.4711 | 15.6908 | 1068.949
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.3603 | 125.0453 | 0.83 | 0.028 | 7.1738 | 25.7542 | 1064.135
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.2902 | 122.1157 | 0.83 | 0.028 | 10.6001 | -0.098259 | 870.7095
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.22 | 134.7627 | 1.821 | 36.8521 | 4.5268 | -0.14402 | 900.9366
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.1499 | 142.0195 | 350.1997 | 70.7896 | 0.76155 | 0.33319 | 907.2243
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.0798 | 141.0818 | 281.2738 | 42.8775 | 0.68755 | -0.083678 | 893.1748
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 86.0097 | 144.3085 | 175.87 | 41.1297 | 0.62809 | -0.099753 | 1039.508
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.9396 | 143.05 | 160.6298 | 40.9786 | 0.6242 | 0.76645 | 1030.996
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.8695 | 144.1205 | 157.7287 | 41.0366 | 0.62774 | 6.3262 | 1043.581
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.7994 | 144.5835 | 159.88 | 41.0893 | 0.63871 | 6.7394 | 1031.573
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.7293 | 265.318 | 160.2983 | 40.996 | 0.63407 | 12.6395 | 1058.812
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.6592 | 247.75 | 160.0222 | 40.9035 | 0.64034 | 18.9155 | 1063.401
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.5891 | 127.7817 | 164.0948 | 41.1374 | 0.62836 | 20.4281 | 1057.548
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.519 | 280.6798 | 160.5053 | 40.9563 | 0.6121 | 21.0207 | 871.9294
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.4488 | 235.2458 | 162.7955 | 41.0798 | 0.62325 | 28.5815 | 943.1224
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.3787 | 168.3037 | 162.3 | 41.331 | 0.63779 | 21.9881 | 1033.666
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.3086 | 145.1907 | 158.752 | 40.771 | 0.69522 | 0.029592 | 1056.056
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.2385 | 142.3572 | 1.8103 | 0.78508 | 2.3258 | -0.15671 | 1061.255
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.1684 | 143.2948 | 0.83 | 0.027 | 2.3258 | -0.10205 | 1041.611
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.0983 | 143.8213 | 0.83 | 0.027 | 60.3223 | -0.61256 | 1036.183
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 85.0282 | 143.0695 | 0.83 | 0.027 | 28.2539 | -0.65419 | 1048.572
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.9581 | 143.0172 | 0.83 | 0.027 | 11.6679 | -0.56783 | 1050.892
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.888 | 144.2282 | 0.83 | 0.027 | 10.9317 | 1.5811 | 1067.901
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.8179 | 142.4952 | 0.83 | 0.027 | 9.8918 | 2.781 | 1066.451
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.7478 | 146.19 | 0.83 | 0.025433 | 7.504 | 4.1667 | 1164.098
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.6776 | 137.2217 | 0.83 | 0.025 | 9.4065 | 7.3829 | 1024.813
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.6075 | 0.83 | 0.83 | 0.025 | 6.7286 | 9.0097 | 1033.186
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.5374 | 0.83 | 0.83 | 0.025 | 7.1923 | 12.269 | 1037.898
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.4673 | 0.83 | 1.566 | 1.2336 | 8.6973 | 13.1164 | 1048.092
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.3972 | 0.83 | 257.5662 | 72.6787 | 0.91059 | 20.5579 | 1025.973
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.3271 | 0.83 | 141.2028 | 72.349 | 0.73698 | -0.068321 | 1036.719
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.257 | 0.83 | 159.5533 | 48.2704 | 0.71584 | -0.096173 | 1041.856
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.1869 | 0.82 | 160.7277 | 40.9349 | 0.64356 | 1.2825 | 1046.74
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.1168 | 0.82 | 161.6722 | 40.8956 | 0.64135 | -0.0037894 | 1051.684
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 84.0467 | 0.82 | 161.3202 | 40.8453 | 0.63981 | -0.059149 | 1006.404
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.9765 | 0.82 | 162.0658 | 40.8835 | 0.64295 | 2.6875 | 985.1463
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.9064 | 0.82 | 162.4497 | 40.993 | 0.63405 | 4.0545 | 1051.923
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.8363 | 0.82 | 162.3155 | 40.877 | 0.65094 | 4.5709 | 1026.88
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.7662 | 0.82 | 161.0215 | 40.8466 | 0.62832 | 9.3657 | 1033.496
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.6961 | 0.82 | 158.8972 | 41.0233 | 0.63474 | 10.2887 | 1031.245
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.626 | 0.82 | 160.46 | 40.302 | 0.65138 | 12.2243 | 1031.94
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.5559 | 0.82 | 160.8549 | 40.8383 | 1.5193 | 15.2955 | 1032.83
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.4858 | 0.82 | 1.8115 | 0.80522 | 50.4839 | 15.2891 | 1031.736
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.4157 | 0.82 | 0.83 | 0.029067 | 50.4839 | 15.1245 | 1047.3
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.3456 | 0.82 | 0.83 | 0.02285 | 58.4958 | -0.074615 | 1066.75
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.2755 | 0.82 | 0.83 | 0.023167 | 33.253 | -0.14985 | 1059.366
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.2053 | 0.82 | 0.83 | 0.023 | 15.5205 | -0.33667 | 859.2554
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.1352 | 0.82 | 0.83 | 0.023 | 11.1049 | -0.51807 | 924.161
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 83.0651 | 0.82 | 0.83 | 0.023 | 11.9385 | -0.53118 | 908.1718
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.995 | 0.82 | 0.83 | 0.023 | 8.348 | 0.85671 | 925.0761
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.9249 | 0.82 | 0.83 | 0.023 | 10.1424 | 3.8126 | 992.4328
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.8548 | 0.82 | 0.83 | 0.023 | 7.7654 | 4.9252 | 1029.748
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.7847 | 0.82 | 0.83 | 0.023917 | 7.3475 | 519.5868 | 1046.874
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.7146 | 0.82 | 1.606 | 1.2107 | 9.0175 | 519.5868 | 1027.061
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.6445 | 0.82 | 247.0683 | 69.8127 | 0.70746 | 519.5868 | 1043.921
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.5744 | 0.82 | 144.425 | 40.7521 | 0.66427 | 519.5868 | 1726.136
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.5042 | 0.82 | 141.3698 | 40.903 | 0.63797 | 474.4282 | 1529.332
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.4341 | 0.82 | 153.9807 | 40.8578 | 0.64983 | 335.3918 | 857.3879
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.364 | 0.82 | 161.1778 | 40.837 | 0.64628 | 162.0615 | 972.3392
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.2939 | 0.82 | 160.195 | 40.8798 | 0.64557 | -0.16663 | 1018.362
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.2238 | 0.82 | 163.2928 | 40.927 | 0.65392 | -0.16247 | 1038.569
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.1537 | 0.82 | 162.1948 | 40.8882 | 0.65862 | 0.09563 | 1022.918
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.0836 | 0.82 | 163.2433 | 40.9517 | 0.65602 | -0.38016 | 1011.85
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 82.0135 | 0.82 | 164.0872 | 41.0271 | 0.63566 | -0.3892 | 1031.375
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.9434 | 0.82 | 297.1015 | 40.9806 | 0.63438 | 2.006 | 1020.958
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.8733 | 0.82 | 392.14 | 42.115 | 0.63067 | 4.7174 | 1044.704
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.8032 | 0.82 | 147.4105 | 40.8536 | 0.7504 | 10.5061 | 1039.928
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.733 | 0.82 | 1.6167 | 0.79662 | 4.3689 | 10.778 | 1039.508
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.6629 | 0.82 | 1.6783 | 0.029 | 4.3689 | 10.8413 | 917.033
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.5928 | 0.82 | 315.7033 | 0.029 | 27.4066 | 11.3776 | 1043.856
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.5227 | 0.82 | 269.4812 | 0.029 | 36.4171 | 12.0136 | 1068.608
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.4526 | 0.82 | 194.1592 | 0.029 | 15.7932 | 12.0136 | 1062.827
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.3825 | 0.82 | 164.454 | 0.029 | 12.5621 | 13.5211 | 1061.97
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.3124 | 0.82 | 161.5215 | 0.029 | 12.1175 | -0.10711 | 1049.042
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.2423 | 0.82 | 162.4512 | 0.029 | 8.293 | -0.16377 | 1058.536
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.1722 | 0.82 | 163.0525 | 0.029 | 10.2453 | -0.26544 | 1069.365
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.1021 | 0.82 | 162.2298 | 0.029 | 7.0494 | -0.65973 | 1080.882
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 81.032 | 0.82 | 161.6363 | 0.029 | 7.4736 | -0.75466 | 1054.089
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.9618 | 0.82 | 161.6212 | 1.2184 | 8.4863 | -0.22711 | 1033.741
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.8917 | 0.82 | 159.6117 | 67.4144 | 0.70809 | 1.9337 | 1645.933
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.8216 | 0.82 | 163.45 | 40.6611 | 0.67958 | 2.7027 | 1089.653
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.7515 | 0.82 | 154.4307 | 40.472 | 0.67429 | 6.4673 | 1035.09
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.6814 | 0.82 | 1.6485 | 40.7071 | 0.64985 | 7.6585 | 1037.43
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.6113 | 0.82 | 0.83 | 40.8074 | 0.63741 | 9.1501 | 1046.247
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.5412 | 0.82 | 0.83 | 40.9122 | 0.63806 | 11.7132 | 1048.535
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.4711 | 0.82 | 0.83 | 40.9128 | 0.64486 | 16.0617 | 1057.161
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.401 | 0.82 | 0.83 | 40.9515 | 0.64904 | 19.4863 | 1053.772
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.3309 | 0.82 | 0.83 | 40.9115 | 0.65838 | -0.13261 | 1061.198
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.2607 | 0.82 | 0.82 | 44.5145 | 0.64225 | -0.15931 | 1067.24
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.1906 | 0.82 | 0.82 | 72.1615 | 0.75068 | -0.15236 | 1080.798
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.1205 | 0.82 | 0.82 | 71.379 | 1.2173 | -0.43905 | 864.3814
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 80.0504 | 0.82 | 0.82 | 44.9245 | 0.76314 | -0.47467 | 1024.406
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.9803 | 0.82 | 0.82 | 0.75627 | 4.453 | -0.24711 | 1039.213
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.9102 | 0.82 | 0.82 | 0.026 | 4.453 | 3.4996 | 1053.893
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.8401 | 0.82 | 0.82 | 0.026 | 4.453 | 4.627 | 1045.208
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.77 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.611
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.6999 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1028.992
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.6298 | 0.82 | 0.82 | 0.026 | 4.453 | 7.9081 | 1034.406
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.5597 | 0.82 | 0.82 | 0.026 | 4.453 | 8.8144 | 1051.324
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.4895 | 0.82 | 0.82 | 0.026 | 4.453 | 11.5816 | 1049.278
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.4194 | 0.82 | 0.82 | 0.026 | 4.453 | 15.2228 | 1055.082
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.3493 | 0.82 | 0.82 | 0.026 | 4.453 | -0.094059 | 877.9323
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.2792 | 0.82 | 0.82 | 0.026 | 17.1926 | -0.12636 | 884.2773
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.2091 | 0.82 | 0.82 | 1.2471 | 51.037 | -0.022934 | 970.1237
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.139 | 0.82 | 0.82 | 72.5447 | 0.69187 | -0.2911 | 1061.106
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 79.0689 | 0.82 | 0.82 | 72.2521 | 0.74228 | -0.33163 | 1058.15
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.9988 | 0.82 | 0.82 | 53.7303 | 0.69685 | -0.32213 | 1056.86
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.9287 | 0.82 | 0.82 | 40.9114 | 0.65995 | -0.32213 | 1040.489
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.8586 | 0.82 | 0.82 | 40.9621 | 0.65312 | -0.22594 | 1033.822
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.7885 | 0.82 | 0.82 | 40.9006 | 0.65033 | -0.059809 | 1071.282
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.7183 | 0.82 | 0.82 | 40.934 | 0.65789 | -0.29741 | 1727.56
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.6482 | 0.82 | 0.82 | 40.9187 | 0.65846 | -0.30991 | 1539.706
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.5781 | 0.82 | 0.82 | 40.9878 | 0.65259 | -0.30991 | 1561.595
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.508 | 0.82 | 0.82 | 40.8562 | 0.64558 | -0.25927 | 1158.264
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.4379 | 0.82 | 0.82 | 40.9364 | 0.64336 | 0.72283 | 1033.918
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.3678 | 0.82 | 0.82 | 40.757 | 0.66113 | -0.040134 | 1032.46
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.2977 | 0.82 | 0.82 | 40.7378 | 0.70649 | -0.16181 | 1046.441
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.2276 | 0.82 | 0.82 | 0.79742 | 1.9423 | -0.22997 | 1036.824
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.1575 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48001 | 1024.879
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.0874 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.56223 | 1042.816
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 78.0172 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.48538 | 1045.783
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 77.9471 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1039.836
CH_PLANT | Tiong Bahru Plaza | 29/7/2024 3:00:00 pm | 77.877 | 0.82 | 0.82 | 0.027 | 1.9423 | -0.46189 | 1043.321
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.8069 | 1.22 | 1.25 | 0.027233 | 2.7188 | -0.34407 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.7368 | 1.22 | 1.25 | 0.023083 | 2.7188 | -0.44403 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.6667 | 1.22 | 1.25 | 0.025833 | 2.7188 | -0.37779 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.5966 | 1.22 | 1.25 | 0.02545 | 2.7188 | -0.38702 | 0.041519
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.5265 | 1.22 | 1.25 | 0.03 | 2.7188 | -0.21799 | 0.039043
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.4564 | 1.22 | 1.25 | 0.029233 | 2.7188 | -0.028549 | 0.030092
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.3863 | 1.22 | 2.3778 | 1.6488 | 2.675 | -0.23414 | 9.0059
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.3162 | 246.5597 | 280.7353 | 70.9599 | 0.73531 | -0.07142 | 1690.326
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.246 | 125.2428 | 145.8425 | 42.7777 | 0.69281 | -0.094762 | 884.9695
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.1759 | 137.1002 | 156.6213 | 40.7826 | 0.68215 | -0.10691 | 952.4618
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.1058 | 139.8893 | 159.1872 | 40.9193 | 0.63479 | -0.11443 | 1041.436
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 77.0357 | 140.8792 | 158.5855 | 41.0393 | 0.62426 | -0.11543 | 1056.731
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.9656 | 221.9605 | 175.607 | 40.9837 | 0.64242 | -0.10769 | 1036.294
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.8955 | 140.2733 | 158.8407 | 41.0056 | 0.63472 | -0.1173 | 1045.249
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.8254 | 142.1052 | 159.8045 | 41.0341 | 0.63285 | -0.12278 | 1059.402
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.7553 | 144.1458 | 161.946 | 41.0707 | 0.63395 | -0.11783 | 1065.612
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.6852 | 141.8417 | 160.1317 | 41.0181 | 0.62181 | -0.1122 | 1069.103
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.6151 | 140.5007 | 159.4812 | 41.0865 | 0.6193 | -0.11926 | 1076.985
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.5449 | 140.57 | 159.04 | 41.579 | 0.62605 | -0.14984 | 1074.193
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.4748 | 141.058 | 158.581 | 40.868 | 0.65829 | -0.14946 | 1044.188
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.4047 | 130.7298 | 148.4518 | 40.915 | 0.67405 | -0.12879 | 935.1829
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.3346 | 117.5178 | 135.1652 | 40.8078 | 0.67383 | -0.12049 | 848.7857
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.2645 | 4.7478 | 6.746 | 3.5104 | 80.5523 | -0.18482 | 45.9688
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.1944 | 0.82 | 0.83 | 0.026 | 100 | -0.38204 | 0.044798
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.1243 | 0.82 | 0.83 | 0.026 | 100 | -0.57364 | 0.061306
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 76.0542 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.9841 | 0.82 | 0.82 | 0.027 | 23.0878 | 0.87323 | 0.028785
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.914 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.8439 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.7737 | 0.82 | 0.82 | 0.027 | 11.7776 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.7036 | 0.82 | 0.82 | 0.027 | 11.7776 | 0.11661 | 0.025362
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.6335 | 0.82 | 1.9465 | 1.2302 | 11.5825 | 0.51479 | 9.1209
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.5634 | 246.4515 | 279.7987 | 71.1543 | 0.72617 | -0.076356 | 1683.885
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.4933 | 128.951 | 149.5775 | 43.0249 | 0.65758 | -0.076843 | 924.5991
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.4232 | 140.4737 | 159.7885 | 41.1052 | 0.63282 | -0.10871 | 1045.377
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.3531 | 142.0907 | 159.883 | 41.0164 | 0.63041 | -0.11496 | 1055.381
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.283 | 186.7575 | 209.186 | 52.5459 | 0.66119 | -0.12783 | 1320.499
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.2129 | 229.7897 | 280.1932 | 70.2844 | 0.79022 | -0.13347 | 1529.901
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.1428 | 142.7257 | 160.3652 | 41.0934 | 0.65049 | -0.097729 | 1009.67
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.0727 | 143.0432 | 160.6148 | 41.1502 | 0.64262 | -0.10625 | 1031.015
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 75.0025 | 142.8107 | 160.6047 | 41.0635 | 0.64257 | -0.12158 | 1047.873
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.9324 | 137.0848 | 154.673 | 41.1465 | 0.61488 | -0.10729 | 1040.055
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.8623 | 144.2362 | 161.8407 | 41.2256 | 0.62414 | -0.1147 | 1076.944
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.7922 | 145.09 | 163.32 | 41.253 | 0.64273 | -0.13513 | 1087.566
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.7221 | 146.2625 | 163.8971 | 40.9539 | 0.69015 | -0.1447 | 1024.106
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.652 | 146.5522 | 164.1902 | 40.9175 | 0.71209 | -0.14608 | 997.3012
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.5819 | 138.7963 | 156.3802 | 40.8798 | 0.7299 | -0.14523 | 930.1482
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.5118 | 5.498 | 7.3932 | 3.4646 | 2.6111 | -0.32653 | 45.4795
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.4417 | 1.22 | 1.25 | 0.026383 | 2.7188 | -0.33104 | 0.040644
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.3716 | 1.22 | 1.25 | 0.028333 | 2.7188 | -0.36589 | 0.045597
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.3014 | 0.83 | 0.84 | 0.027 | 8.0352 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.2313 | 0.83 | 0.84 | 0.027 | 6.0026 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.1612 | 0.83 | 0.84 | 0.027 | 6.4372 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.0911 | 0.83 | 0.84 | 0.027 | 7.6552 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 74.021 | 0.83 | 0.84 | 0.027 | 5.9199 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.9509 | 0.83 | 0.84 | 0.027 | 6.5571 | 99.8743 | 0.005589
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.8808 | 126.4015 | 144.7565 | 36.9302 | 4.5121 | 148.3259 | 1012.239
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.8107 | 235.68 | 270.4148 | 70.8428 | 0.76277 | -0.16582 | 1586.328
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.7406 | 128.2073 | 148.9905 | 43.1212 | 0.64724 | -0.069869 | 931.3377
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.6705 | 140.3597 | 159.8255 | 41.0614 | 0.61835 | -0.10981 | 1066.461
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.6004 | 140.4878 | 159.98 | 40.9684 | 0.62014 | -0.11648 | 1074.682
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.5302 | 142.4567 | 161.7275 | 41.0075 | 0.62356 | -0.11888 | 1081.214
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.4601 | 144.5543 | 162.1173 | 41.0789 | 0.62663 | -0.11935 | 1079.576
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.39 | 243.5245 | 272.3382 | 66.4408 | 0.71871 | -0.14597 | 1636.203
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.3199 | 226.2037 | 258.6357 | 72.4902 | 0.72466 | -0.12683 | 1520.699
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.2498 | 221.4017 | 253.6505 | 72.3899 | 0.72347 | -0.12106 | 1495.992
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.1797 | 229.7897 | 261.58 | 72.3516 | 0.7556 | -0.12189 | 1556.079
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.1096 | 228.8565 | 262.6715 | 72.3883 | 0.71446 | -0.12175 | 1543.966
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 73.0395 | 237.11 | 269.65 | 71.217 | 0.82068 | -0.22467 | 1554.615
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.9694 | 133.7517 | 153.9242 | 45.4351 | 0.73477 | -0.1109 | 924.9098
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.8993 | 98.7822 | 116.3917 | 40.7715 | 0.85827 | 0.0521 | 652.1562
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.8291 | 129.5563 | 147.1483 | 40.9378 | 0.70292 | -0.11715 | 880.2216
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.759 | 7.033 | 9.184 | 4.0991 | 86.5351 | -0.062333 | 56.7134
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.6889 | 0.82 | 0.82 | 0.027 | 98.9909 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.6188 | 0.82 | 0.82 | 0.027 | 100 | -0.062022 | 0.028785
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.5487 | 206.7068 | 0.83 | 0.026 | 100 | -0.10313 | 0.058996
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.4786 | 119.4613 | 0.83 | 0.026 | 100 | -0.10437 | 0.051369
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.4085 | 127.997 | 0.83 | 0.026 | 100 | -0.10663 | 0.039262
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.3384 | 142.6465 | 0.83 | 0.026 | 100 | -0.11741 | 0.031919
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.2683 | 143.6025 | 0.83 | 0.026 | 100 | -0.11923 | 0.021833
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.1982 | 142.7458 | 0.83 | 0.026 | 100 | -0.11557 | 0.018015
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.1281 | 142.711 | 2.0462 | 1.8698 | 98.3347 | -0.12244 | 14.3597
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 72.0579 | 143.444 | 239.0118 | 66.3348 | 0.7121 | -0.11332 | 1471.32
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.9878 | 141.6845 | 138.9158 | 40.703 | 0.66909 | -0.11467 | 1030.919
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.9177 | 140.6642 | 147.4525 | 40.7007 | 0.68017 | -0.10844 | 963.0865
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.8476 | 139.9377 | 162.0748 | 40.9712 | 0.64095 | -0.14722 | 837.8268
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.7775 | 143.29 | 162.7395 | 41.0033 | 0.64729 | -0.10044 | 55.4017
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.7074 | 146.4534 | 160.4697 | 40.9327 | 0.64575 | -0.11629 | 0.028136
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.6373 | 136.036 | 160.4998 | 41.0982 | 0.6411 | -0.11738 | 0.033642
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.5672 | 116.7468 | 158.82 | 40.996 | 0.6267 | -0.10962 | 0.033642
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.4971 | 6.6235 | 159.3763 | 41.0776 | 0.64652 | -0.10489 | 0.033642
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.427 | 215.058 | 159.158 | 41.1763 | 0.62255 | -0.11367 | 0.026509
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.3569 | 126.2693 | 159.4637 | 41.1472 | 0.61775 | -0.11977 | 0.023204
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.2867 | 128.0323 | 161.14 | 39.873 | 0.6625 | -0.1197 | 0.023204
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.2166 | 129.9807 | 164.3364 | 40.8911 | 0.6848 | -0.11356 | 0.023204
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.1465 | 126.395 | 153.8458 | 40.8832 | 0.69066 | -0.12636 | 5.0644
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.0764 | 144.8175 | 134.6227 | 40.8122 | 0.67318 | -0.16058 | 1498.723
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 71.0063 | 140.8467 | 8.7743 | 4.1022 | 89.6044 | -0.083317 | 1014.502
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.9362 | 143.6355 | 0.83 | 0.024 | 100 | -0.10831 | 926.9705
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.8661 | 140.895 | 0.83 | 0.024 | 100 | -0.085801 | 836.9425
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.796 | 141.4633 | 0.83 | 0.024 | 100 | -0.10097 | 42.5944
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.7259 | 141.7427 | 0.83 | 0.024 | 100 | -0.10685 | 0.035437
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.6558 | 139.28 | 0.83 | 0.024 | 100 | -0.097822 | 0.040601
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.5856 | 142.3341 | 0.83 | 0.024 | 100 | -0.10488 | 0.040601
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.5155 | 133.021 | 0.83 | 0.024 | 100 | -0.10985 | 0.004186
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.4454 | 120.5402 | 0.83 | 0.024 | 100 | -0.10527 | 0.004186
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.3753 | 4.8203 | 1.6648 | 1.0708 | 98.3418 | -0.1056 | 0.004186
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.3052 | 1.23 | 246.5468 | 62.1118 | 0.70046 | -0.13159 | 0.004186
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.2351 | 1.23 | 147.2463 | 42.6844 | 0.70715 | -0.094844 | 0.004186
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.165 | 1.23 | 147.6903 | 40.7043 | 0.6873 | -0.099375 | 0.004186
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.0949 | 1.23 | 149.5338 | 40.6594 | 0.69365 | -0.10072 | 998.849
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 70.0248 | 1.23 | 146.0702 | 40.7871 | 0.68061 | -0.10409 | 1573.417
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 69.9547 | 1.23 | 164.332 | 40.9224 | 0.65052 | -0.10938 | 1038.827
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 69.8846 | 124.83 | 160.1183 | 41.0297 | 0.64509 | -0.10075 | 0.2601
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 69.8144 | 228.9153 | 161.2775 | 40.9836 | 0.64635 | -0.10879 | 0.031902
CH_PLANT | Causeway Point | 29/7/2024 3:00:00 pm | 69.7443 | 122.3367 | 158.7487 | 40.8822 | 0.64482 | -0.10923 | 0.047766